## DATA
Date/time | ID | L | MT | Heat Load on staves |  |  | PRESSURES[bara] | [11 empty] | temperatures [oC] |  |  |  | Power on | Temp. after | Press. After
Vic and Rich | mm | m | (measured) | Ps1 | Ps2 | PsT | pressures on HE | [5 empty] | pressures bef/aft capillary | [5 empty] | of liquid |  | of vapor |  | the heater | the heater | the heater
[7 empty] | of liquid |  | Dpliq | of vapor |  | Dpvap | HP_man | LP_man | LP_9 | LP_7 | L9_after | LP_7after | T0 | T1 | T3 | T4 | PH | T5 | Pheater
|  |  | [g/s] | [W] | [W] | [W] | bef. HE | after HE_bfC |  | bef. HE | after HE |  |  |  | bef _stave | bef _stave | after stave | aft stave | bef. HE | after HE | bef. HE | after HE | [W]
Heat exchanger model LBL C1
07.10.2003 |  | L09
17:13 | 0.88 | 2.34 | 3.86 | 0 | 0 | 0 | 14.5 | 14.25 | 0.25 | 1.68 | 1.7 | -0.02 | 14.25 | 1.88 | 1.84 | 0 | 1.89 | 0 | 27 | -14.42 | -23.65 | -24.31 | ~600 | 23.7 | 0
|  | L07 | [14 empty] | 1.756
08.10.2003 | 0.88 | 3 | 3.05 | 0 | 0 | 0 | 14.8 | 14.6 |  | 1.66 | 1.66 |  | 14.6 | 1.84 |  | 1.77 |  | 1.84 | 40.15 | -13.87 | 23.63 | -24.06 | ~600 | 23.56 | 0
10:00
50%
11:35 | 0.88 | 3 | 3.11 | 48.85 | 48.85 | 97.7 | 13.75 | 13.5 | 0.25 | 1.67 | 1.65 | 0.02 | 13.5 | 1.91 |  | 1.86 |  | 1.9 | 40 | -13.07 | -23.3 | -8.9 | ~600 | 24.23 | 0
100%
12:10 | 0.88 | 3 |  | 97 | 97 | 194 | [6 empty] | 13.5 |  | not enough LQ, , ie. Fluid
12:22 | 0.88 | 3 |  | 97 | 97 | 194 | [6 empty] | 15 |  |  |  | Q
13:10 | 0.88 | 3 | 2.93 | 97 | 97 | 194 | 15.1 | 15 | 0.1 | 1.65 | 1.64 | 0.01 | 15 | 1.97 |  | 1.98 | -0.16156 | 1.97 | 39.64 | 11.48 | -24.9 | 18.59 | ~600 | 24.9 | 0
13:30
slight increase of the liq inlet pressure from 15 to 15.5 bara
| and back again @ 13:50 to 15 bara |  |  |  |  | 100%
14:10 | 0.88 | 3 | 3 | 97 | 97 | 194 | 15 | 14.9 | 0.1 | 1.66 | 1.64 | 0.02 | 14.9 | 1.98 |  | 1.99 |  | 1.99 | 39.6 | 5.79 | -22.19 | 16.62 | ~600 | 25 | 0
JUST BEFORE THE POWER GAMES
JUMP FROM 100% TO 50% POWER | [5 empty] | 50%
15:05 | 0.88 | 3 | 3.2 | 48.85 | 48.85 | 97.7 | 15 | 14.8 | 0.2 | 1.72 | 1.69 | 0.03 | 14.8 | 1.91 |  | 1.91 |  | 1.95 | 39 | -13.8 | -21.65 | -12.93 | ~600 | 22.1 | 0
JUMP BACK TO 100% POWER | [5 empty] | 100%
16:05 | 0.88 | 3 | !!2.8!! | 97 | 97 | 194 | 14.7 | 14.8 | -0.1 | 1.64 | 1.63 | 0.01 | 14.8 | 1.95 |  | 1.95 |  | 1.95 | 39.6 | 14.5 | -13.8 | 21 | ~600 | 24.9 | 0
Note: BOX still at -13.5 C
CORRECTION OF INLET PRESSURE | [16 empty] | Q
16:10BEFORE CAPIL_ TO 15.5 bara | [12 empty] | 15.5 |  |  |  | 0.098723
16:30:00 Additional correction
BEFORE CAPIL_ TO 16 bara |  |  | 3.2 | [9 empty] | 16
Stable again @ | [5 empty] | 100% | [10 empty] | Q
17:30 | 0.88 | 3 | 3.3 | 97 | 97 | 194 | 16.1 | 15.9 | 0.2 | 1.72 | 1.68 | 0.04 | 15.9 | 2.03 |  | 2.04 | -0.15951 | 2.03 | 39.61 | -2 | -21.3 | 12 | ~600 | 24 | 0
Note: BOX still at -13.5 C | [12 empty] | Cap_T_in | -2.13
JUMP FROM 100% TO 50% POWER | [5 empty] | 50% | [6 empty] | Cap_T_out | -3.17
17:45 | 0.88 | 3 | 3.5 | 48.85 | 48.85 | 97.7 | 16.1 | 16 | 0.1 | 1.73 | 1.71 | 0.02 | 16 | 1.95 |  | 1.93 |  | 1.98 | 39.22 | -12.8 | -21.2 | -14 | ~600 | 26 | 0
[13 empty] | Cap_T_in | -12.8
[13 empty] | Cap_T_out | -12.5
JUMP BACK from 50%TO 100% POWER | [5 empty] | 100% | [10 empty] | Q
18:15 | 0.88 | 3 | 3.35 | 97 | 97 | 194 | 16 | 15.8 | 0.2 | 1.7 | 1.68 | 0.02 | 15.9 | 2.04 |  | 2.04 | -0.14567 | 2.04 | 39.23 | -2.82 | -21.3 | 11.3 | ~600 | 25 | 0
Note: BOX still at -13.5 C | [12 empty] | Cap_T_in | -2.88
JUMP FROM 100% TO 0% POWER | [5 empty] | 0% | [6 empty] | Cap_T_out | -3.6 |  |  | Q
18:45:00 PM | 0.88 | 3 | 3.5 | 0 | 0 | 0 | 16.1 | 16 | 0.1 | 1.71 | 1.7 | 0.01 | 16 | 1.87 |  | 1.84 | -0.20539 | 1.9 | 38.9 | -12.98 | -21.73 | -23.5 | ~600 | 25 | 0
[13 empty] | Cap_T_in | -12.96
[13 empty] | Cap_T_out | -12.66
JUMP BACK from 0%TO 100% POWER | [5 empty] | 100%
| 0.88 | 3 | 3.4 | 97 | 97 | 194 | 16.1 | 15.9 | 0.2 | 1.7 | 1.68 | 0.02 | 15.9 | 2.04 |  | 2.05 |  | 2.04 | 39.4 | -2.44 | -21.5 | 11.6 | ~600 | 25
[13 empty] | Cap_T_in | -2.68
| slight DECREASE of the liq inlet pressure from 16 to 15.5 bara 7:35:00 PM | [11 empty] | Cap_T_out | -3.55
100%
Stiil at 100% POWER | 0.88 | 3 | 3.16 | 97 | 97 | 194 | 15.5 | 15.3 | 0.2 | 1.68 | 1.66 | 0.02 | 15.3 | 2.03 |  | 2.04 |  | 2.03 | 39.15 | 0.77 | -21.7 | 14 | ~600 | 25
reduced flow a) |  | appr | 3.2 | [9 empty] | Cap_T_in | 0.77
19:55 |  | appr | 3.1 | [9 empty] | Cap_T_out
Note: BOX still at -13.5 C | [5 empty] | 50% | [10 empty] | Q
JUMP FROM 100% TO 50% POWER | 0.88 | 3 | 3.45 | 48.85 | 48.85 | 97.7 | 15.7 | 15.5 | 0.2 | 1.72 | 1.7 | 0.02 | 15.5 | 1.94 |  | 1.93 | -0.16895 | 1.96 | 38.9 | -13.2 | -21.5 | -13.4 | ~600 | 23
20:00 |  | appr | 3.45 | [9 empty] | Cap_T_in | -13.2
[13 empty] | Cap_T_out | -12.8
Note: BOX still at -13.5 C | [5 empty] | 100% | [10 empty] | Q
JUMP BACK from 50%TO 100% POWER | 0.88 | 3 | 3.2 | 97 | 97 | 194 | 15.5 | 15.4 | 0.1 | 1.68 | 1.66 | 0.02 | 15.4 | 2.02 |  | 2.02 | -0.14863 | 2.02 | 39.15 | -0.81 | -21.56 | 13.03 | ~600 | 25
20:25 |  | appr | 3.22 | [9 empty] | Cap_T_in | -1
|  | appr | 3.22 | [9 empty] | Cap_T_out | -2.3
No power, no heating of the liquid, same inlet press as for 100% power, and approx same temp on the stave
[6 empty] | 0% | [10 empty] | Q
| 0.88 | 3 | 3.43 | 0 | 0 | 0 | 15.6 | 15.5 | 0.1 | 1.84 | 1.82 | 0.02 | 15.5 | 2.01 |  | 1.95 | -0.22071 | 2.02 | 30 | -12.6 | -20.4 | -21.9 | ~600 | 28
21:15 |  | appr
appr