## DATA
Date/time | ID | L | MT | Heat Load on staves |  |  | PRESSURES[bara] | [11 empty] | temperatures [oC] |  |  |  | Power on | Temp. after | Press. After
Vic and Rich | mm | m | (measured) | Ps1 | Ps2 | PsT | pressures on HE | [5 empty] | pressures bef/aft capillary | [5 empty] | of liquid |  | of vapor |  | the heater | the heater | the heater
[7 empty] | of liquid |  | Dpliq | of vapor |  | Dpvap | HP_man | LP_man | LP_9 | LP_7 | L9_after | LP_7after | T0 | T1 | T3 | T4 | PH | T5 | Pheater
|  |  | [g/s] | [W] | [W] | [W] | bef. HE | after HE_bfC |  | bef. HE | after HE |  |  |  | bef _stave | bef _stave | after stave | aft stave | bef. HE | after HE | bef. HE | after HE | [W]
Heat exchanger model LBL C1
07.10.2003 |  | L09
17:13 | 0.88 | 2.34 | 3.86 | 0 | 0 | 0 | 14.5 | 14.25 | 0.25 | 1.68 | 1.7 | -0.02 | 14.25 | 1.88 | 1.84 | 0 | 1.89 | 0 | 27 | -14.42 | -23.65 | -24.31 | ~600 | 23.7 | 0
|  | L09 | [14 empty] | 1.756
Aluminum Capillary | 0.88 | 2.34
09.10.2003
Works without pump, to keep low mass flow
| 0.88 | 2.34 | 3.36 | 0 | 0 | 0 | 11.25 | 11 | 0.25 | 1.7 | 1.66 | 0.04 | 11 | 1.85 | 1.82 |  | 1.89 |  | 31.25 | -13.76 | -23.3 | -24 | ~600 | 24 | 0
10:00 |  | approx | 3.78 | [9 empty] | bef_cap | -13.75 |  |  | 1.77
power_0W |  | approx | 3.62 | [9 empty] | after_cap | -13.82
|  | approx | 3.39
Jump to 50% Power | [5 empty] | 50%
11:35 | 0.88 | 2.34 | 3.37 | 48.85 | 48.85 | 97.7 | 11.25 | 11 | 0.25 | 1.7 | 1.67 | 0.03 | 11 | 1.93 | 1.9 |  | 1.95 |  | 30.7 | -14 | -22.7 | -23.8 | 600 | 25 | 0
[13 empty] | bef_cap | -13.97 |  |  | 1.827
12:55 | [12 empty] | after_cap | 14.01
Jump to 100% Power | [5 empty] | 100% | [11 empty] | Q
12:55 | 0.88 | 2.34 |  | 97 | 97 | 194 | 11.2 | 11 | 0.2 | 1.7 | 1.675 | 0.025 | 11 | 1.99 | 1.98 |  | 1.99 | -0.20265
13:15 |  | approx | 3.23 | [9 empty] | bef_cap
13:30 |  | approx | 3.14 | [9 empty] | after_cap
13:35 |  | approx | 2.8
does not stabilize with PbfCap at 11 bara, increased by 1 bar to 12 bara and LiQ_in at 35 C
| SEARCH FOR OTIMAL FLOE AND PARAMETERS |  |  |  |  | 100%
13:40 | 0.88 | 2.34 |  | 97 | 97 | 194 | 12.15 | 12 | 0.15 |  |  |  | 12 | 1.95 | 1.96 |  | 1.93
13:50 |  | approx | 2.8 | [13 empty] | 1.805
14:00 |  | approx | 2.9
14:10 |  | approx | 3.19 | [11 empty] | 2.03 |  | 2.01
| SEARCH FOR OTIMAL FLOE AND PARAMETERS |  |  |  |  | 100% | [11 empty] | Q
| 0.88 | 2.34 | 3.25 | 97 | 97 | 194 | 12.25 | 12 | 0.25 | 1.68 | 1.66 | 0.02 | 12 | 2 | 2.01 |  | 1.99 | -0.20562 | 37 | -2.3 | -21.75 | 12.04 | 600 | 25 | stable
14:33 |  | approx | 3.25 | [9 empty] | bef_cap | -1.63 |  |  | 1.865
|  | approx | [10 empty] | after_cap | -6.01
approx
Jump to 50% Power | [5 empty] | 50% | [11 empty] | Q
11:35 | 0.88 | 2.34 | 3.45 | 48.85 | 48.85 | 97.7 | 12.25 | 12 | 0.25 | 1.72 | 1.68 | 0.04 | 12 | 1.96 | 1.93 |  | 1.98 | -0.21908 | 36 | -13.1 | -21.4 | -17.6 | 600 | 27 | stable
|  | approx | [10 empty] | bef_cap | -13.1 |  |  | 1.84
|  | approx | [10 empty] | after_cap | -13.3
Jump from 100% to 0% Power | [5 empty] | 100%
| 0.88 | 2.34 |  | 97 | 97 | 194
50%
11:35 | 0.88 | 3 | 3.11 | 48.85 | 48.85 | 97.7 | 13.75 | 13.5 | 0.25 | 1.67 | 1.65 | 0.02 | 13.5 | 1.91 |  | 1.86 |  | 1.9 | 40 | -13.07 | -23.3 | -8.9 | ~600 | 24.23 | 0
100%
12:10 | 0.88 | 3 |  | 97 | 97 | 194 | [6 empty] | 13.5 |  | not enough LQ, , ie. Fluid
12:22 | 0.88 | 3 |  | 97 | 97 | 194 | [6 empty] | 15 |  |  |  | Q
13:10 | 0.88 | 3 | 2.93 | 97 | 97 | 194 | 15.1 | 15 | 0.1 | 1.65 | 1.64 | 0.01 | 15 | 1.97 |  | 1.98 | -0.16156 | 1.97 | 39.64 | 11.48 | -24.9 | 18.59 | ~600 | 24.9 | 0
13:30
slight increase of the liq inlet pressure from 15 to 15.5 bara
| and back again @ 13:50 to 15 bara |  |  |  |  | 100%
14:10 | 0.88 | 3 | 3 | 97 | 97 | 194 | 15 | 14.9 | 0.1 | 1.66 | 1.64 | 0.02 | 14.9 | 1.98 |  | 1.99 |  | 1.99 | 39.6 | 5.79 | -22.19 | 16.62 | ~600 | 25 | 0
JUST BEFORE THE POWER GAMES
JUMP FROM 100% TO 50% POWER | [5 empty] | 50%
15:05 | 0.88 | 3 | 3.2 | 48.85 | 48.85 | 97.7 | 15 | 14.8 | 0.2 | 1.72 | 1.69 | 0.03 | 14.8 | 1.91 |  | 1.91 |  | 1.95 | 39 | -13.8 | -21.65 | -12.93 | ~600 | 22.1 | 0
JUMP BACK TO 100% POWER | [5 empty] | 100%