## Sheet1
Date / Time | date/time |  | 13:29 | 13:53 | 14:15 | 15:38 | 16:09 | 16:41 | 17:14 | barrel coopling loop measurements - started 1/12/2004 = -45deg geom | 15:06 | 15:15 | 15:55 |  | 16:50 | 17:22 | 18:02 | 18:18 | 19:00 | 19:16 | 19:32 | 2004-03-12 | 14:50 | 15:22 | 15:42 | 15:47 | 16:14 | 16:25 | 16:55 | 17:09 | 17:17 | 2004-07-12 | 11:50 | 12:05 power to full |  | 14:45 | 15:01 | 15:08 | 15:30 | 15:38 | 16:12 | dropped pressure to 11.75 | 2004-08-12 | 11:14 | 11:23 | 11:51 | 11:57 | 12:16 | 12:26 | 12:55 | 12:58 | 17:00 | 17:20 | 17:30 | 17:38 | 17:59 | 18:12 | 18:23 | 2004-09-12 | 15:29 | 15:35 | 16:07 | 16:16 | 16:52 | 17:06 | 17:25 | 17:27 | 17:45 | 17:55 | 18:00
mass flow | by Danfoss | [6 empty] | vol flow 8.7 to 8.82 depends on numbers in massflow.xls | [27 empty] | drop pressure by 0.5bar |  | drop pressure by 0.5bar |  | drop pressure by 0.5bar |  | system got hot |  |  | 100% power |  | adjust pressure to get 7.8g/s |  | power to 554W (10% extra) |  | turned power down and went to lunch | BACK |  | power to 15% extra | power to 100% | power to 110% |  | system off |  |  | turn power off! |  | power to 100% | 7.79 taken 16:40 to 16:50 | adjusted TlbHEX slightly |  | reduce TlbHEX to 20C |  | power off
by energy balance
| by Volume / time |  | 8.23 | 8.22 | 8.23 | 7.78 | 8.16 | 8.82 | 8.78 |  | 8.7 |  | 8.61 |  | 8.68 |  | 8.06 |  | 7.9 |  | 8.75 |  | 7.82 |  | 8.85 |  | 8.77 |  | 7.88 |  | 8.25 |  | 8.1 |  | 7.9 |  | 7.7 |  | 7.42 |  | 6.78 | failed to cool last module on top loop |  | 8.14 |  | 8.01 |  | 7.85 |  | 7.37 |  | power to 1.09* | 7.39 | modules not cooled correctly! | 7.76 |  | 7.28 |  |  | 7.76 |  | 8.72 |  | 7.74 | things are stable | 7.72 |  | 8.67 |  | 8.84
Characteristic values: | Power on staves |  | 0% | 52.91% | 72.89% | 102% | 0% | 0% | 0% |  | 0% |  | 55.42% |  | 75.69% |  | 89.52% |  | 99.41% |  | 0% |  | 0% |  | 0% |  | 101.5% |  | 101.5% |  | 0% |  | 0% |  | 100.9% |  | 100.9% |  | 100.9% |  | 99.55% | pc crashed - finish for today |  | 0% |  | 100.8% |  | 100.8% |  | 109.5% |  |  | 108.9% |  | 100% |  | 110.7% |  |  | 100.2% |  | 0% |  | 99.92% |  | 99.92% |  | 99.92% |  | 0%
| Inlet temp into HEX |  | 34.295 | 34.1605 | 34.6485 | 34.7585 | 34.997 | 22.583 | 35.3085 |  | 35.7155 |  | 35.227 |  | 35.536 |  | 34.812 |  | 35.3455 |  | 35.3955 |  | 19.7465 |  | 21.456 |  | 22.287 |  | 20.865 |  | 20.7565 |  | 19.4275 |  | 19.506 |  | 19.33 |  | 19.654 |  | 19.9365 |  |  | 19.8945 |  | 19.8975 |  | 19.8865 |  | 20.692 |  |  | 20.27 |  | 20.007 |  | 20.2645 |  |  | 35.368 |  | 34.5895 |  | 35.376 |  | 35.438 |  | 21.9315 |  | 22.4005
| Massflow |  | 8.23 | 8.22 | 8.23 | 7.78 | 8.16 | 8.82 | 8.78 |  | 8.7 |  | 8.61 |  | 8.68 |  | 8.06 |  | 7.9 |  | 8.75 |  | 7.82 |  | 8.85 |  | 8.77 |  | 7.88 |  | 8.25 |  | 8.1 |  | 7.9 |  | 7.7 |  | 7.42 |  | 6.78 |  |  | 8.14 |  | 8.01 |  | 7.85 |  | 7.37 |  |  | 7.39 |  | 7.76 |  | 7.28 |  |  | 7.76 |  | 8.72 |  | 7.74 |  | 7.72 |  | 8.67 |  | 8.84
Pressures | before capillary (manometer) |  | 17.5 | 17.5 | 17.6 | 17.5 | 17.3 | 17.5 | 17.3 |  | 15.7 |  | 15.7 |  | 15.9 |  | 15.7 |  | 16.25 |  | 16.25 |  | 12.9 |  | 16.3 |  | 15.5 |  | 13.75 |  | 13.75 |  |  |  | 13.8 |  | 13.3 |  | 12.6 |  | 12 |  |  | 14.2 |  | 14.2 |  |  |  | 13.7 |  |  | 13.7 |  | 13.7 |  | 13.75 |  |  | 16.2 |  | 16.2 |  | 16.2 |  | 16.2 |  | 16.2 |  | 16.2
differential accorss caps | DP #1 DiffPCAP (00.06) |  | 15.676 | 15.572 | 15.632 | 15.547 | 15.571 | 15.663 | 15.377 |  | 13.477 | temp | 13.195 | temp | 13.284 | temp | 12.999 | temp | 13.473 | temp | 14.064 | temp | 10.965 | temp | 14.156 | temp | 13.743 | temp | 11.214 | temp | 11.742 | temp | 11.752 | temp | 11.309 | temp | 10.85 | temp | 10.153 | temp | 9.676 | temp |  | 12.149 | temp | 11.659 | temp | 11.153 | temp | 11.197 | temp |  | 11.166 | temp | 11.127 | temp | 11.176 | temp |  | 13.47 | temp | 13.977 | temp | 13.369 | temp | 13.403 | temp | 13.444 | temp | 13.971 | temp
after capillaries | Abs PlaCAP (00.01) |  | 1.769 | 1.867 | 1.889 | 1.809 | 1.757 | 1.8 | 1.828 |  | 2.166 | -18.5725 | 2.461 | -15.0248 | 2.575 | -13.742 | 2.627 | -13.172 | 2.7 | -12.3874 | 2.19 | -18.2709 | 1.978 | -21.0208 | 2.087 | -19.5826 | 2.679 | -12.6113 | 2.482 | -14.785 | 1.962 | -21.2364 | 1.993 | -20.8198 | 2.498 | -14.6033 | 2.505 | -14.5242 | 2.426 | -15.4282 | 2.363 | -16.1657 |  | 2.005 | -20.6597 | 2.51 | -14.4677 | 2.472 | -14.899 |  | -59.329 |  | 2.514 | -14.4226 | 2.468 | -14.9447 | 2.504 | -14.5355 |  | 2.662 | -12.7936 | 2.2 | -18.1459 | 2.817 | -11.1663 | 2.66 | -12.8151 | 0.2655 | -52.5032 | 2.089 | -19.5567
Cap temperatures | before cap0 (05.25) |  | 1.912 | 3.112 | 3.6 | 10.7 | 2.293 | -18.78 | -17.24 |  | -7.059 |  | -6.975 |  | -5.09 |  | 6.321 |  | 11.289 |  | -7.272 |  | -13.72 |  | -12.08 |  | -9.246 |  | -10.61 |  | -14.16 |  | -13.86 |  | -10.8 |  | -10.97 |  | -10.17 |  | 1.901 |  |  | -13.54 |  | -11.01 |  | -11.07 |  | 1.122 |  |  | 0.304 |  | -11.087 |  | 1.932 |  |  | 11.576 |  | -4.345 |  | 11.194 |  | 12.065 |  | 9.766 |  | -12.68
| before cap1 (05.08) |  | 1.148 | 1.836 | 3.487 | 12.531 | 1.36 | -18.02 | -16.51 |  | -5.215 |  | -6.153 |  | -5.354 |  | 6.533 |  | 12.335 |  | -5.947 |  | -13.43 |  | -12.03 |  | -9.492 |  | -10.11 |  | -15.01 |  | -13.57 |  | -11 |  | -10.88 |  | -9.827 |  | 2.188 |  |  | -13.21 |  | -10.89 |  | -10.75 |  | 1.662 |  |  | 0.734 |  | -10.43 |  | 2.216 |  |  | 12.593 |  | -5.969 |  | 12.155 |  | 13.115 |  | -10.49 |  | -14.12
| average TlbCAP |  | 1.53 | 2.474 | 3.5435 | 11.6155 | 1.8265 | -18.4 | -16.875 |  | -6.137 |  | -6.564 |  | -5.222 |  | 6.427 |  | 11.812 |  | -6.6095 |  | -13.575 |  | -12.055 |  | -9.369 |  | -10.36 |  | -14.585 |  | -13.715 |  | -10.9 |  | -10.925 |  | -9.9985 |  | 2.0445 |  |  | -13.375 |  | -10.95 |  | -10.91 |  | 1.392 |  |  | 0.519 |  | -10.7585 |  | 2.074 |  |  | 12.0845 |  | -5.157 |  | 11.6745 |  | 12.59 |  | -0.362 |  | -13.4
| after cap0 (05.21) |  | 1.55 | 2.215 | 3.826 | 12.212 | 1.735 | -16.94 | -15.47 |  | -4.661 |  | -4.444 |  | -2.88 |  | 7.367 |  | 11.674 |  | -4.494 |  | -10.48 |  | -9.292 |  | -6.258 |  | -7.446 |  | -10.53 |  | -10.15 |  | -7.602 |  | -7.742 |  | -7.206 |  | 3.384 |  |  | -10.21 |  | -7.853 |  | -7.903 |  | 2.668 |  |  | 2.092 |  | -7.664 |  | 3.339 |  |  | 11.702 |  | -2.216 |  | 11.433 |  | 12.167 |  | -6.509 |  | -8.985
| after cap1 (05.16) |  | 3.05 | 4.199 | 4.67 | 10.588 | 3.498 | -15.87 | -14.39 |  | -3.16 |  | -4.083 |  | -3.255 |  | 7.574 |  | 12.755 |  | -3.742 |  | -10.5 |  | -9.344 |  | -6.862 |  | -7.46 |  | -11.86 |  | -10.51 |  | -8.299 |  | -8.148 |  | -7.198 |  | 3.65 |  |  | -10.51 |  | -8.299 |  | -8.181 |  | 2.944 |  |  | 2.075 |  | -7.908 |  | 3.487 |  |  | 12.918 |  | -4.066 |  | 12.558 |  | 13.434 |  | -8.008 |  | -11.42
| average TlaCAP |  | 2.3 | 3.207 | 4.248 | 11.4 | 2.6165 | -16.405 | -14.93 |  | -3.9105 |  | -4.2635 |  | -3.0675 |  | 7.4705 |  | 12.2145 |  | -4.118 |  | -10.49 |  | -9.318 |  | -6.56 |  | -7.453 |  | -11.195 |  | -10.33 |  | -7.9505 |  | -7.945 |  | -7.202 |  | 3.517 |  |  | -10.36 |  | -8.076 |  | -8.042 |  | 2.806 |  |  | 2.0835 |  | -7.786 |  | 3.413 |  |  | 12.31 |  | -3.141 |  | 11.9955 |  | 12.8005 |  | -7.2585 |  | -10.2025
HEX efficiency/temps | TlbHEX (05.24) |  | 34.353 | 34.225 | 34.689 | 34.796 | 35.059 | 22.675 | 35.333 |  | 35.776 |  | 35.283 |  | 35.535 |  | 34.751 |  | 35.244 |  | 35.445 |  | 19.655 |  | 21.38 |  | 22.195 |  | 20.71 |  | 20.671 |  | 19.332 |  | 19.371 |  | 19.17 |  | 19.482 |  | 19.733 |  |  | 19.806 |  | 19.778 |  | 19.756 |  | 20.52 |  |  | 20.085 |  | 19.862 |  | 20.074 |  |  | 35.272 |  | 34.661 |  | 35.288 |  | 35.339 |  | 21.837 |  | 22.832
| TlbHEX (05.26) |  | 34.237 | 34.096 | 34.608 | 34.721 | 34.935 | 22.491 | 35.284 |  | 35.655 |  | 35.171 |  | 35.537 |  | 34.873 |  | 35.447 |  | 35.346 |  | 19.838 |  | 21.532 |  | 22.379 |  | 21.02 |  | 20.842 |  | 19.523 |  | 19.641 |  | 19.49 |  | 19.826 |  | 20.14 |  |  | 19.983 |  | 20.017 |  | 20.017 |  | 20.864 |  |  | 20.455 |  | 20.152 |  | 20.455 |  |  | 35.464 |  | 34.518 |  | 35.464 |  | 35.537 |  | 22.026 |  | 21.969
| average TlbHEX |  | 34.295 | 34.1605 | 34.6485 | 34.7585 | 34.997 | 22.583 | 35.3085 |  | 35.7155 |  | 35.227 |  | 35.536 |  | 34.812 |  | 35.3455 |  | 35.3955 |  | 19.7465 |  | 21.456 |  | 22.287 |  | 20.865 |  | 20.7565 |  | 19.4275 |  | 19.506 |  | 19.33 |  | 19.654 |  | 19.9365 |  |  | 19.8945 |  | 19.8975 |  | 19.8865 |  | 20.692 |  |  | 20.27 |  | 20.007 |  | 20.2645 |  |  | 35.368 |  | 34.5895 |  | 35.376 |  | 35.438 |  | 21.9315 |  | 22.4005
| TlaHEX (05.22) | [9 empty] | -9.951 |  | -10.06 |  | -8.32 |  | 2.287 |  | 7.504 |  | -10.26 |  | -16.73 |  | -15.15 |  | -12.1 |  | -13.81 |  | -17.36 |  | -16.84 |  | -13.82 |  | -14.03 |  | -13.59 |  | -2.384 |  |  | -15.99 |  | -13.96 |  | -14.18 |  | -3.031 |  |  | -3.929 |  | -14.21 |  | -2.01 |  |  | 8.007 |  | -7.796 |  | 7.471 |  | 8.673 |  | -12.67 |  | -15.33
| TlaHEX (05.07) |  | -1.43 | -0.767 | 0.84 | 9.38 | -1.246 | -19.46 | -18.03 |  | -7.599 |  | -8.652 |  | -7.789 |  | 2.771 |  | 8.429 |  | -7.995 |  | -15.4 |  | -13.9 |  | -11.43 |  | -12.51 |  | -16.93 |  | -15.47 |  | -13.12 |  | -13.05 |  | -12.28 |  | -1.681 |  |  | -14.94 |  | -12.84 |  | -13.07 |  | -2.06 |  |  | -3.003 |  | -12.72 |  | -1.402 |  |  | 8.938 |  | -9.186 |  | 8.368 |  | 9.609 |  | -12.43 |  | -15.66
| average TlaHEX |  | -1.43 | -0.767 | 0.84 | 9.38 | -1.246 | -19.46 | -18.03 |  | -8.775 |  | -9.356 |  | -8.0545 |  | 2.529 |  | 7.9665 |  | -9.1275 |  | -16.065 |  | -14.525 |  | -11.765 |  | -13.16 |  | -17.145 |  | -16.155 |  | -13.47 |  | -13.54 |  | -12.935 |  | -2.0325 |  |  | -15.465 |  | -13.4 |  | -13.625 |  | -2.5455 |  |  | -3.466 |  | -13.465 |  | -1.706 |  |  | 8.4725 |  | -8.491 |  | 7.9195 |  | 9.141 |  | -12.55 |  | -15.495
| TvbHEX (05.19) |  | -23.86 | -22.39 | -22.12 | -23.37 | -23.92 | -24.46 | -23.84 |  | -21.67 |  | -20.46 |  | -20.61 |  | -22.57 |  | -22.825 |  | -21.77 |  | -23.03 |  | -21.94 |  | -19.84 |  | -22.38 |  | -23.69 |  | -22.92 |  | -21.53 |  | -22.13 |  | -23.15 |  | -24.34 |  |  | -22.46 |  | -21.78 |  | -22.3 |  | -23.91 |  |  | -23.96 |  | -22.54 |  | -24.11 |  |  | -23.12 |  | -22.11 |  | -23.02 |  | -23.16 |  | -20.54 |  | -22.26
| TvaHEX (05.18) | copy of measurements with dummy heat load | -25.51 | -25.28 | -12.54 | 13.48 | -25.7 | -24.33 | -24.27 |  | -22.85 |  | -21.31 |  | -7.969 |  | 6.764 |  | 13.578 |  | -23.23 |  | -23.83 |  | -22.98 |  | -19.02 |  | -7.261 |  | -24.78 |  | -24.07 |  | -10.71 |  | -8.209 |  | -4.056 |  | 4.29 |  |  | -23.56 |  | -12.33 |  | -8.527 |  | 2.981 |  |  | 1.924 |  | -7.635 |  | 3.792 |  |  | 14.009 |  | -23.5 |  | 13.589 |  | 14.492 |  | -17.5 |  | -23.21
| HEX efficiency |  | 0.61283 | 0.60054 | 0.58646 | 0.43191 | 0.60408 | 0.90254 | 0.89934 |  | 0.77086 |  | 0.77906 |  | 0.77102 |  | 0.55841 |  | 0.46926 |  | 0.76244 |  | 0.83776 |  | 0.80936 |  | 0.80526 |  | 0.77568 |  | 0.84684 |  | 0.83867 |  | 0.7758 |  | 0.77652 |  | 0.74653 |  | 0.49439 |  |  | 0.80556 |  | 0.79474 |  | 0.7814 |  | 0.51995 |  |  | 0.53616 |  | 0.76061 |  | 0.49635 |  |  | 0.45303 |  | 0.75461 |  | 0.46242 |  | 0.44243 |  | 0.80317 |  | 0.83469
Other Pressures | DP #2 across HEX vapor (00.03) |  | 0.105 | 0.155 | 0.169 | 0.148 | 0.1 | 0.074 | 0.108 |  | 0.204 |  | 0.271 |  | 0.3 |  | 0.265 |  | 0.257 |  | 0.187 |  | 0.156 |  | 0.193 |  | 0.316 |  | 0.272 |  | 0.182 |  | 0.186 |  | 0.273 |  | 0.262 |  | 0.248 |  | 0.2 |  |  | 0.189 |  | 0.293 |  | 0.268 |  | 0.238 |  |  | 0.238 |  | 0.277 |  | 0.237 |  |  | 0.256 |  | 0.24 |  | 0.258 |  | 0.256 |  | 0.311 |  | 0.164
| DP #3 over upper loop (00.04) | [9 empty] | 0.275 |  | 0.465 |  | 0.567 |  | 0.744 |  | 0.821 |  | 0.286 |  | 0.156 |  | 0.18 |  | 0.616 |  | 0.601 |  | 0.176 |  | 0.194 |  | 0.589 |  | 0.585 |  | 0.59 |  | 0.638 |  |  | 0.154 |  | 0.575 |  | 0.592 |  | 0.734 |  |  | 0.729 |  | 0.603 |  | 0.739 |  |  | 0.821 |  | 0.264 |  | 0.814 |  | 0.821 |  | 0.61 |  | 0.2
| DP #4 across HEX liquid (00.05) |  | 0.141 | 0.144 | 0.142 | 0.115 | 0.129 | 0.172 | 0.147 |  | 0.16 | temp | 0.167 | temp | 0.165 | temp | 0.139 | temp | 0.148 | temp | 0.166 | temp | 0.127 | temp | 0.171 | temp | 0.173 | temp | 0.14 | temp | 0.148 | temp | 0.144 | temp | 0.155 | temp | 0.116 | temp | 0.116 | temp | 0.113 | temp |  | 0.14 | temp | 0.145 | temp | 0.139 | temp | 0.121 | temp |  | 0.123 | temp | 0.139 | temp | 0.125 | temp |  | 0.141 | temp | 0.17 | temp | 0.145 | temp | 0.154 | temp | 0.163 | temp | 0.17 | temp
| Pressure at Exhaust manifold (Keller) | [9 empty] | 1.85 | -22.7788 | 2 | -20.7263 | 1.99 | -20.8599 | 1.845 | -22.849 | 1.825 | -23.1312 | 1.92 | -21.808 | 1.83 | -23.0605 | 1.92 | -21.808 | 2.05 | -20.0649 | 1.86 | -22.6387 | 1.79 | -23.6296 | 1.83 | -23.0605 | 1.92 | -21.808 | 1.88 | -22.3599 | 1.8 | -23.4866 | 1.71 | -24.7916 |  | 1.87 | -22.4991 | 1.9 | -22.083 | 1.86 | -22.6387 | 1.75 | -24.2066 |  | 1.75 | -24.2066 | 1.85 | -22.7788 | 1.735 | -24.425 |  | 1.81 | -23.3441 | 1.9 | -22.083 | 1.82 | -23.202 | 1.805 | -23.4153 | 2.01 | -20.5931 | 1.91 | -21.9452
| DP of lower loop (calculated) | [9 empty] | 0.316 |  | 0.461
| Abs P before HEX (00.00) | [9 empty] | 1.885 |  | 1.942 |  | 1.918 |  | 1.771 |  | 1.76 |  | 1.866 |  | 1.803 |  | 2.096 |  | 1.975 |  | 1.805 |  | 1.745 |  | 1.754 |  | 1.851 |  | 1.81 |  | 1.73 |  | 1.639 |  |  | 1.831 |  | 1.837 |  | 1.807 |  | 1.674 |  |  | 1.682 |  | 1.781 |  | 1.668 |  |  | 1.747 |  | 1.843 |  | 1.752 |  | 1.738 |  | 1.948 |  | 1.838
| pressure before BPR (00.02) |  | 1.27 | 1.284 | 1.281 | 1.233 | 1.28 | 1.36 | 1.354 |  | 1.343 |  | 1.368 |  | 1.325 |  | 1.239 |  | 1.232 |  | 1.325 |  | 1.384 |  | 1.365 |  | 1.367 |  | 1.249 |  | 1.303 |  | 1.336 |  | 1.324 |  | 1.296 |  | 1.265 |  | 1.259 |  |  | 1.38 |  | 1.277 |  | 1.253 |  | 1.189 |  |  | 1.189 |  | 1.241 |  | 1.18 |  |  | 1.212 |  | 1.336 |  | 1.217 |  | 1.21 |  | 1.313 |  | 1.33
| press drop over exhaust | [9 empty] | 0.080097 |  | -20.19 |  | 0.19767 |  | 0.27293 |  | 0.28646 |  | 0.029813 |  | -0.021558 |  | -0.025909 |  | 0.22364 |  | 0.23132 |  | 0.0019527 |  | 0.027859 |  | 0.2248 |  | 0.22903 |  | 0.22785 |  | 0.22085 |  |  | -0.020203 |  | 0.21874 |  | 0.22891 |  | 0.26533 |  |  | 0.26846 |  | 0.2309 |  | 0.27098 |  |  | 0.28212 |  | 0.15781 |  | 1.1692 |  | 0.28632 |  | 0.22709 |  | -0.0017175
| over loop (DP#3 - DP exhaust) | [9 empty] | 0.1949 |  | 20.655 |  | 0.36933 |  | 0.47107 |  | 0.53454 |  | 0.25619 |  | 0.17756 |  | 0.20591 |  | 0.39236 |  | 0.36968 |  | 0.17405 |  | 0.16614 |  | 0.3642 |  | 0.35597 |  | 0.36215 |  | 0.41715 |  |  | 0.1742 |  | 0.35626 |  | 0.36309 |  | 0.46867 |  |  | 0.46054 |  | 0.3721 |  | 0.46802 |  |  | 0.53888 |  | 0.10619 |  | -0.35519 |  | 0.53468 |  | 0.38291 |  | 0.20172
| over loop from T on loop | [9 empty] | 0.13884 | 0.18817 | 3.06 | 0.22783 | 0.2656 | 0.27941 | 0.46284 | 0.46435 | 0.52439 | 0.52592 | 0.14954 | 0.19737 | 0.065619 | 0.074901 | 0.080197 | -5.9743 | 0.19598 | 0.21267 | 0.23059 | 0.25378 | 0.078417 | 0.084502 | 0.064694 | 0.10767 | 0.20768 | 0.22979 | 0.21201 | 0.24334 | 0.2475 | 0.28353 | 0.39976 | 0.40302 |  | 0.059983 | 0.082933 | 0.20317 | 0.22685 | 0.21049 | 0.2431 | 0.43793 | -0.44919 |  | 0.42847 | 0.43549 | 0.22195 | 0.26243 | 0.44456 | 0.4544 |  | 0.52083 | 0.52535 | 0.06093 | 0.18254 | -0.36957 | 0.51959 | 0.52544 | 0.52725 | 0.1981 | 0.20317 | 0.076786 | 0.078583
Detector heating | Volts |  | 0 | 134 | 155 | 185 | 0 | 0 | 0
| Current |  | 0 | 1.99 | 2.37 | 2.78 | 0 | 0 | 0
| Power on detector structure [W] |  | 0 | 266.66 | 367.35 | 514.3 | 0 | 0 | 0 |  | 0 |  | 279.3 |  | 381.5 |  | 451.2 |  | 501.02 |  | 0 |  | 0 |  | 0 |  | 511.422 |  | 511.422 |  | 0 |  | 0 |  | 508.416 |  | 508.416 |  | 508.416 |  | 501.707 |  |  | 0 |  | 508.149 |  | 508.149 |  | 551.984 |  |  | 549.053 |  | 504.137 |  | 558.057 |  |  | 505.04 |  | 0 |  | 503.619 |  | 503.619 |  | 503.619 |  | 0
nominal power = 504W | % |  | 0 | 0.52909 | 0.72887 | 1.0204 | 0 | 0 | 0 |  | 0 |  | 0.55417 |  | 0.75694 |  | 0.89524 |  | 0.99409 |  | 0 |  | 0 |  | 0 |  | 1.0147 |  | 1.0147 |  | 0 |  | 0 |  | 1.0088 |  | 1.0088 |  | 1.0088 |  | 0.99545 |  |  | 0 |  | 1.0082 |  | 1.0082 |  | 1.0952 |  |  | 1.0894 |  | 1.0003 |  | 1.1073 |  |  | 1.0021 |  | 0 |  | 0.99924 |  | 0.99924 |  | 0.99924 |  | 0
Vapor heater after HEX | Volts |  | pid -100V | pid -100V | pid -100V | pid -100V | pid -100V | pid -100V | pid -100V |  | pid - 100V |  | pid 100V |  | pid 100V |  | pid 100V |  | pid 100V |  | pid 100V |  | pid 100V |  | pid 100V |  | pid 100V |  | pid 100V |  | pid 100V |  | pid 100V |  | pid 100V |  | pid 100V |  | pid 100V |  | pid 100V |  |  | pid 100V |  | pid 100V |  | pid 100V |  | pid 100V |  |  | pid 100V |  | pid 100V |  | pid 100V |  |  | pid 100V |  | pid 100V |  | pid 100V |  | pid 100V |  | pid 100V |  | pid 100V
| Current |  | 80% | 45% | 35% | 12% | 78% | 95% | 85% |  | 78% |  | 48% |  | 35% |  | 21% |  | 16% |  | 78% |  | 93% |  |  |  | 33% |  | 23.7% |  | 86% |  | 88% |  | 26% |  | 25% |  | 20% |  | 13% |  |  | 95% |  | 26% |  | 27% |  | 15% |  |  | 15% |  | 23% | [6 empty] | 86% |  | 7% |  | 6% |  | 31% |  | 95%
Power P=VI
Power on heater | P=V2/R, R=14 - need tocheck
| Temp after vapor heater (05.21) |  |  |  | 24.3 | 25.116 | 21.3 | 17.4 | 20.89 |  | 25.847 |  | 27.8 |  | 28.7 |  | 29.2 |  | 30 |  | 26.2 |  | 24.05 |  | 19.959 |  | 19.62 |  | 19.5 |  | 25.2 |  | 23.91 |  | 19.667 |  | 19.515 |  | 20.066 |  | 20.66 |  |  | 24.559 |  | 19.33 |  | 19.459 |  | 20.521 |  |  | 20.527 |  | 19.521 |  | 20.606 |  |  | 19.9 |  | 25.864 |  | 20.875 |  | 19.732 |  | 19.223 |  | 25.228
| Tlbmass flow meter (05.20) |  | 24.6 | 24.5 | 24.7 | 24.7 | 24.9 | 25.1 | 25.7 |  | 22.4 |  | 22.6 |  | 22.6 |  | 22.7 |  | 22.69 |  | 22.7 |  | 23.174 |  | 23.3 |  | 23.4 |  | 21.1 |  | 23.1 |  | 21.97 |  | 21.588 |  | 21.774 |  | 21.919 |  | 22.2 |  |  | 21.942 |  | 21.7 |  | 20.073 |  | 21.732 |  |  | 21.398 |  | 20.247 |  | 21.981 |  |  | 22.3 |  | 21.891 |  | 22.32 |  | 22.16 |  | 22.06 |  | 22
| temp in massflow meter (manual) |  | ---- | ---- | ---- | ---- | ---- | ---- | ---- |  | --- | [60 empty] | ----
Cooling loop temperatures | [11 empty] | pressure |  | pressure |  | pressure |  | pressure |  | pressure |  | pressure |  | pressure |  | pressure |  | pressure |  | pressure |  | pressure |  | pressure |  | pressure |  | pressure |  | pressure |  | pressure |  |  | pressure |  | pressure |  | pressure |  | pressure |  |  | pressure |  | pressure |  | pressure |  |  | pressure |  | pressure |  | pressure |  | pressure |  | pressure |  | pressure
upper loop | Inlet temp CaTe01 (06.00) | [9 empty] | -19.65 | 2.0689 | -16.5 | 2.3315 | -15.13 | 2.4533 | -13.75 | 2.5808 | -13.17 | 2.6358 | -19.27 | 2.0994 | -22.19 | 1.8741 | -20.86 | 1.9743 | -14.95 | 2.4696 | -16.61 | 2.3219 | -22.24 | 1.8704 | -21.54 | 1.9226 | -16.26 | 2.3525 | -16.62 | 2.321 | -17.15 | 2.2753 | -16.51 | 2.3306 |  | -21.71 | 1.9098 | -16.61 | 2.3219 | -16.87 | 2.2994 | -15.13 | 2.4533 |  | -15.2 | 2.4469 | -16.83 | 2.3029 | -15.16 | 2.4505 |  | -13.41 | 2.613 | -19.03 | 2.1187 | -13.34 | 2.6196 | -13.37 | 2.6168 | -15.33 | 2.4352 | -20.72 | 1.9851
| Inlet after 1st heater MoTe24 (06.12) | [9 empty] | -19.96 | 2.0444 | -16.36 | 2.3437 | -14.92 | 2.4724 | -13.89 | 2.5676 | -13.43 | 2.6111 | -19.54 | 2.0777 | -22.63 | 1.8418 | -21.19 | 1.9491 | -14.59 | 2.5026 | -16.34 | 2.3455 | -22.71 | 1.8359 | -21.82 | 1.9016 | -15.88 | 2.386 | -16.24 | 2.3542 | -16.76 | 2.3089 | -16.58 | 2.3245 |  | -21.94 | 1.8926 | -16.13 | 2.3639 | -16.38 | 2.342 | -15.13 | 2.4533 |  | -15.16 | 2.4505 | -16.36 | 2.3437 | -15.18 | 2.4487 |  | -13.64 | 2.5912 | -19.31 | 2.0961 | -13.56 | 2.5987 | -13.6 | 2.5949 | -14.88 | 2.476 | -21.01 | 1.9628
| middle of loop CaTe01 (06.03) | [9 empty] | -20 | 2.0412 | -16.2 | 2.3578 | -15.03 | 2.4623 | -15.08 | 2.4578 | -14.93 | 2.4714 | -19.52 | 2.0793 | -22.14 | 1.8778 | -20.82 | 1.9774 | -13.9 | 2.5667 | -15.86 | 2.3878 | -22.03 | 1.8859 | -21.01 | 1.9628 | -15.31 | 2.437 | -15.75 | 2.3976 | -16.62 | 2.321 | -17.69 | 2.2295 |  | -21.43 | 1.9309 | -15.57 | 2.4136 | -15.93 | 2.3816 | -16.27 | 2.3516 |  | -16.23 | 2.3551 | -15.94 | 2.3807 | -16.35 | 2.3446 |  | -15.23 | 2.4442 | -19.55 | 2.0769 | -15.13 | 2.4533 | -15.19 | 2.4478 | -14.15 | 2.5433 | -20.44 | 2.0068
| before last heater CaTe01 (06.06) | [9 empty] | -21.2 | 1.9483 | -18.36 | 2.1736 | -17.65 | 2.2329 | -18.54 | 2.1587 | -18.61 | 2.153 | -20.91 | 1.9704 | -22.88 | 1.8236 | -21.69 | 1.9113 | -16.58 | 2.3245 | -18.82 | 2.1358 | -23.12 | 1.8063 | -22.17 | 1.8755 | -18.17 | 2.1893 | -18.66 | 2.1489 | -19.65 | 2.0689 | -21.01 | 1.9628 |  | -22.29 | 1.8667 | -18.45 | 2.1662 | -18.86 | 2.1326 | -19.83 | 2.0546 |  | -19.8 | 2.057 | -18.97 | 2.1236 | -20.02 | 2.0396 |  | -18.85 | 2.1334 | -18.75 | 2.1415 | -7.203 | 3.2561 | -18.87 | 2.1317 | -17.03 | 2.2856 | -21.49 | 1.9263
| after last heater CaTe04 (06.08) | [9 empty] | -21.44 | 1.9301 | -18.83 | 2.135 | -18.19 | 2.1877 | -19.04 | 2.1179 | -19.12 | 2.1115 | -21.18 | 1.9498 | -23.09 | 1.8084 | -21.92 | 1.8941 | -17.17 | 2.2736 | -19.37 | 2.0913 | -23.32 | 1.792 | -22.41 | 1.8579 | -18.71 | 2.1448 | -19.15 | 2.109 | -20.17 | 2.0278 | -21.43 | 1.9309 |  | -22.52 | 1.8498 | -19.03 | 2.1187 | -19.4 | 2.0889 | -20.33 | 2.0153 |  | -20.29 | 2.0185 | -19.5 | 2.0809 | -20.45 | 2.006 |  | -19.36 | 2.0921 | -19.79 | 2.0578 | -9.654 | 2.9892 | -19.37 | 2.0913 | -17.6 | 2.2371 | -21.73 | 1.9083
| 1st heater MoTe13 (06.01) | [9 empty] | -17.2 |  | -8.7 |  | -6.064 |  | -4.648 |  | -4.35 |  | -16.21 |  | -19.66 |  | -18.39 |  | -4.598 |  | -5.882 |  | -18.92 |  | -17.61 |  | -5.425 |  | -5.755 |  | -6.35 |  | -6.609 |  |  | -18.91 |  | -5.986 |  | -6.119 |  | -5.463 |  |  | -5.524 |  | -5.986 |  | -5.513 |  |  | -4.521 |  | -16.05 |  | -4.433 |  | -4.461 |  | -4.648 |  | -16.91
| 2nd heater PiTe06 (06.02) | [9 empty] | -18.68 |  | -6.18 |  | -2.874 |  | -1.408 |  | 1.427 |  | -17.98 |  | -21.02 |  | -19.73 |  | 1.933 |  | 0.185 |  | -20.62 |  | -19.49 |  | 0.471 |  | 0.081 |  | -0.6 |  | -1.353 |  |  | -20.3 |  | 0.301 |  | -0.024 |  | 2.537 |  |  | 2.526 |  | 0.086 |  | 2.483 |  |  | 0.944 |  | -18.05 |  | 1.02 |  | 0.987 |  | 1.526 |  | -19
| 3rd heater MoTe13 (06.04) | [9 empty] | -18.85 |  | -8.4 |  | -5.159 |  | -4.373 |  | -4.532 |  | -18.15 |  | -20.91 |  | -19.66 |  | -2.613 |  | -4.534 |  | -20.47 |  | -19.24 |  | -4.008 |  | -4.423 |  | -5.303 |  | -6.626 |  |  | -20.15 |  | -4.096 |  | -4.44 |  | -5.392 |  |  | -5.364 |  | -4.501 |  | -5.613 |  |  | -4.75 |  | -18.4 |  | -4.683 |  | -4.722 |  | -2.839 |  | -19.01
| 4th heater PiTe06 (06.05) | [9 empty] | -18.91 |  | -11.44 |  | -9.298 |  | -9.215 |  | -7.568 |  | -18.07 |  | -20.69 |  | -19.5 |  | -5.739 |  | -7.574 |  | -20.14 |  | -18.84 |  | -7.054 |  | -7.458 |  | -8.331 |  | -9.85 |  |  | -19.9 |  | -7.43 |  | -7.651 |  | -7.071 |  |  | -6.972 |  | -7.579 |  | -7.115 |  |  | -8.22 |  | -18.45 |  | -8.055 |  | -8.104 |  | -5.982 |  | -18.6
| penultimate heater CaTe01 (06.06) | [9 empty] | -19.22 |  | -9.719 |  | -6.998 |  | -6.582 |  | -6.987 |  | -18.44 |  | -20.75 |  | -19.65 |  | -4.303 |  | -6.35 |  | -20.3 |  | -19.02 |  | -5.812 |  | -6.233 |  | -7.236 |  | -8.855 |  |  | -20.01 |  | -6.161 |  | -6.494 |  | -7.924 |  |  | -7.879 |  | -6.594 |  | -8.096 |  |  | -7.231 |  | -18.75 |  | -7.209 |  | -7.342 |  | -4.919 |  | -18.68
| last heater CaTe04 (06.08) | [9 empty] | -20.04 |  | -11.4 |  | -9.051 |  | -8.929 |  | -9.372 |  | -19.44 |  | -21.55 |  | -20.45 |  | -6.745 |  | -8.852 |  | -21.34 |  | -20.23 |  | -8.305 |  | -8.797 |  | -9.687 |  | -11.58 |  |  | -20.92 |  | -8.576 |  | -8.963 |  | -10.46 |  |  | -10.34 |  | -9.018 |  | -10.68 |  |  | -9.809 |  | -19.78 |  | -9.681 |  | -9.842 |  | -7.281 |  | -19.81
lower loop | Inlet temp MoTe13 (06.10) | [9 empty] | -18.98 | 2.1228 | -16.17 | 2.3604 | -15.06 | 2.4596 | -13.82 | 2.5742 | -13.23 | 2.6301 | -18.56 | 2.1571 | -21.89 | 1.8963 | -20.53 | 1.9998 | -14.87 | 2.4769 | -16.39 | 2.3411 | -22.09 | 1.8815 | -20.84 | 1.9758 | -16.12 | 2.3648 | -16.39 | 2.3411 | -16.84 | 2.302 | -16.49 | 2.3324 |  | -21.26 | 1.9437 | -16.32 | 2.3472 | -16.54 | 2.328 | -15.1 | 2.456 |  | -15.2 | 2.4469 | -16.41 | 2.3393 | -15.12 | 2.4542 |  | -13.43 | 2.6111 | -19.04 | 2.1179 | -13.44 | 2.6101 | -13.41 | 2.613 | -15.33 | 2.4352 | -20.59 | 1.9951
| Inlet after 1st heater MoTe14 (06.15) | [9 empty] | -18.94 | 2.126 | -15.85 | 2.3887 | -14.63 | 2.4989 | -13.61 | 2.594 | -13.36 | 2.6177 | -18.35 | 2.1744 | -21.82 | 1.9016 | -20.37 | 2.0122 | -14.09 | 2.5489 | -15.62 | 2.4092 | -21.96 | 1.8911 | -20.81 | 1.9781 | -15.48 | 2.4217 | -15.67 | 2.4047 | -16.02 | 2.3736 | -16.27 | 2.3516 |  | -21.14 | 1.9529 | -15.53 | 2.4172 | -15.89 | 2.3851 | -14.86 | 2.4778 |  | -14.84 | 2.4797 | -15.79 | 2.394 | -14.86 | 2.4778 |  | -13.32 | 2.6215 | -19.14 | 2.1098 | -13.32 | 2.6215 | -13.34 | 2.6196 | -14.55 | 2.5063 | -20.4 | 2.0099
| middle of loop PiTe06 (06.13) | [9 empty] | -15.17 | 2.4496 | -11.47 | 2.8025 | -9.864 | 2.9671 | -9.44 | 3.0118 | -9.19 | 3.0384 | -13.58 | 2.5968 | -17 | 2.2882 | -15.97 | 2.378 | -9.181 | 3.0393 | -10.11 | 2.9414 | -15.66 | 2.4056 | -13.63 | 2.5921 | -9.33 | 3.0235 | -9.71 | 2.9833 | -10.45 | 2.9062 | -11.35 | 2.8145 |  | -16.11 | 2.3657 | -10.43 | 2.9083 | -10.33 | 2.9186 | -10.28 | 2.9238 |  | -10.32 | 2.9196 | -9.996 | 2.9533 | -10.21 | 2.931 |  | -9.79 | 2.9749 | -14.55 | 2.5063 | -9.754 | 2.9787 | -9.567 | 2.9984 | -8.653 | 3.0961 | -14.27 | 2.5321
| before last heater MoTe26 (06.17) | [9 empty] | -21.03 | 1.9613 | -18.27 | 2.181 | -17.62 | 2.2354 | -18.46 | 2.1653 | -18.51 | 2.1612 | -20.73 | 1.9843 | -22.7 | 1.8367 | -21.58 | 1.9195 | -16.55 | 2.3271 | -18.79 | 2.1383 | -23 | 1.8149 | -22 | 1.8881 | -18.18 | 2.1885 | -18.6 | 2.1538 | -19.61 | 2.0721 | -20.85 | 1.9751 |  | -22.11 | 1.88 | -18.32 | 2.1769 | -18.8 | 2.1374 | -12.3 | 2.7201 |  | -19.66 | 2.0681 | -18.8 | 2.1374 | -19.83 | 2.0546 |  | -18.75 | 2.1415 | -21.04 | 1.9605 | -18.72 | 2.144 | -18.77 | 2.1399 | -16.91 | 2.296 | -21.36 | 1.9361
| after last heater OuTe01 (06.19) | [9 empty] | -21.38 | 1.9346 | -18.86 | 2.1326 | -18.28 | 2.1802 | -19.14 | 2.1098 | -19.21 | 2.1042 | -21.05 | 1.9597 | -22.91 | 1.8214 | 21.8 | 7.974 | -17.28 | 2.2642 | -19.42 | 2.0873 | -23.25 | 1.797 | -22.27 | 1.8682 | -18.83 | 2.135 | -19.29 | 2.0977 | -20.29 | 2.0185 | -21.45 | 1.9293 |  | -22.37 | 1.8608 | -19.01 | 2.1204 | -19.45 | 2.0849 | -10.46 | 2.9052 |  | -20.38 | 2.0114 | -19.55 | 2.0769 | -20.53 | 1.9998 |  | -19.44 | 2.0857 | -21.37 | 1.9354 | -19.38 | 2.0905 | -19.44 | 2.0857 | -17.66 | 2.232 | -21.62 | 1.9165
| 1st heater MoTe19 (06.11) | [9 empty] | -18.53 |  | -8.93 |  | -5.891 |  | -4.463 |  | -4.308 |  | -17.9 |  | -21.15 |  | -19.9 |  | -3.77 |  | -4.939 |  | -21.2 |  | -19.88 |  | -4.966 |  | -5.177 |  | -5.548 |  | -6.356 |  |  | -20.55 |  | -5.171 |  | -5.36 |  | -5.166 |  |  | -5.36 |  | -5.431 |  | -5.371 |  |  | -4.44 |  | -18.41 |  | -4.402 |  | -4.468 |  | -4.507 |  | -19.72
| 2nd heater CaTe01 (06.14) | [9 empty] | -17.87 |  | -8.5 |  | -5.592 |  | -4.943 |  | -5.105 |  | -16.84 |  | -19.64 |  | -18.54 |  | -2.971 |  | -4.571 |  | -19.02 |  | -17.52 |  | -3.927 |  | -9.721 |  | -5.176 |  | -6.519 |  |  | -18.92 |  | -4.449 |  | -4.676 |  | -5.542 |  |  | -5.48 |  | -4.596 |  | -5.548 |  |  | -5.037 |  | -17.35 |  | -4.976 |  | -4.987 |  | -3.082 |  | -17.55
| penultimate heater MoTe01 (06.16) | [9 empty] | -20.29 |  | -12.89 |  | -10.89 |  | -11.12 |  | -11.41 |  | -19.72 |  | -21.87 |  | -20.77 |  | -8.933 |  | -10.98 |  | -21.85 |  | -20.62 |  | -10.33 |  | -10.81 |  | -11.72 |  | -13.3 |  |  | -21.27 |  | -10.65 |  | -10.97 |  | -12.3 |  |  | -12.27 |  | -11.13 |  | -12.56 |  |  | -11.64 |  | -20.17 |  | -11.59 |  | -11.69 |  | -9.293 |  | -20.26
| last heater PiTe07 (06.18) | [9 empty] | -20.23 |  | -11.65 |  | -9.21 |  | -9.066 |  | -9.382 |  | -19.54 |  | -21.52 |  | -20.48 |  | -6.842 |  | -8.95 |  | -21.41 |  | -20.42 |  | -8.445 |  | -8.883 |  | -9.848 |  | -11.58 |  |  | -21.13 |  | -8.767 |  | -9.144 |  | -10.45 |  |  | -10.39 |  | -9.26 |  | -10.74 |  |  | -9.848 |  | -20.24 |  | -9.87 |  | -9.909 |  | -7.547 |  | -20.32
VQ inlet |  |  | 28.36% | 27.96% | 28.85% | 37.79% | 28.76% | 8.705% | 9.66% |  | 19.25% |  | 16.22% |  | 19.35% |  | 32.79% |  | 38.19% |  | 19.35% |  | 13.65% |  | 13.82% |  | 14.71% |  | 16.31% |  | 13.56% |  | 13.72% |  | 14.9% |  | 15.52% |  | 17.35% |  | 30.12% |  |  | 13.21% |  | 15.02% |  | 15.58% |  | 28.95% |  |  | 28.22% |  | 16.11% |  | 29.8% |  |  | 38.56% |  | 20.75% |  | 38.13% |  | 39.13% |  | 14.65% |  | 13.18%
VQ outlet |  |  | 28.36% | 59.87% | 72.81% | 102.5% | 28.76% | 8.705% | 9.66% |  | 19.25% |  | 48.73% |  | 62.98% |  | 87.8% |  | 100.4% |  | 19.35% |  | 13.65% |  | 13.82% |  | 72.84% |  | 80.15% |  | 13.56% |  | 13.72% |  | 78.49% |  | 80.55% |  | 84.48% |  | 102.2% |  |  | 13.21% |  | 77.62% |  | 79.28% |  | 102% |  |  | 100.7% |  | 79.95% |  | 104.5% |  |  | 102.3% |  | 20.75% |  | 101.9% |  | 103% |  | 72.35% |  | 13.18%
Hliq_sat |  |  | 174.2287 | 175.8614 | 176.1613 | 174.7729 | 174.1621 | 173.5623 | 174.2509 |  | 176.9166 |  | 179.8155 |  | 177.8385 |  | 175.6615 |  | 175.3783 |  | 176.5501 |  | 175.1506 |  | 176.3612 |  | 178.6937 |  | 175.8725 |  | 174.4175 |  | 175.2728 |  | 176.8166 |  | 176.1502 |  | 175.0173 |  | 173.6956 |  |  | 175.7837 |  | 176.539 |  | 175.9614 |  | 174.1732 |  |  | 174.1176 |  | 175.6948 |  | 173.951 |  |  | 175.0506 |  | 176.1724 |  | 175.1617 |  | 175.0062 |  | 177.9162 |  | 176.0058
Hvap_sat |  |  | 276.6843 | 277.5311 | 277.6867 | 276.9665 | 276.6497 | 276.3386 | 276.6958 |  | 278.0784 |  | 279.582 |  | 278.5566 |  | 277.4274 |  | 277.2805 |  | 277.8883 |  | 277.1624 |  | 277.7904 |  | 279.0002 |  | 277.5369 |  | 276.7822 |  | 277.2258 |  | 278.0266 |  | 277.6809 |  | 277.0933 |  | 276.4077 |  |  | 277.4908 |  | 277.8825 |  | 277.583 |  | 276.6554 |  |  | 276.6266 |  | 277.4447 |  | 276.5402 |  |  | 277.1106 |  | 277.6924 |  | 277.1682 |  | 277.0875 |  | 278.5969 |  | 277.606
Hdiff_sat |  |  | 102.4556 | 101.6697 | 101.5254 | 102.1936 | 102.4876 | 102.7763 | 102.4449 |  | 101.1618 |  | 99.7665 |  | 100.7181 |  | 101.7659 |  | 101.9022 |  | 101.3382 |  | 102.0118 |  | 101.4291 |  | 100.3065 |  | 101.6643 |  | 102.3647 |  | 101.953 |  | 101.2099 |  | 101.5307 |  | 102.076 |  | 102.7122 |  |  | 101.7071 |  | 101.3436 |  | 101.6216 |  | 102.4823 |  |  | 102.509 |  | 101.7499 |  | 102.5892 |  |  | 102.06 |  | 101.52 |  | 102.0065 |  | 102.0813 |  | 100.6807 |  | 101.6002
Hliq_end_cap |  |  | 203.2846 | 204.292 | 205.4483 | 213.392 | 203.6361 | 182.509 | 184.1472 |  | 196.3866 |  | 195.9945 |  | 197.3229 |  | 209.0275 |  | 214.2966 |  | 196.1561 |  | 189.0788 |  | 190.3805 |  | 193.4438 |  | 192.452 |  | 188.2957 |  | 189.2565 |  | 191.8994 |  | 191.9055 |  | 192.7307 |  | 204.6363 |  |  | 189.2231 |  | 191.76 |  | 191.7978 |  | 203.8466 |  |  | 203.0441 |  | 192.0821 |  | 204.5208 |  |  | 214.4027 |  | 197.2413 |  | 214.0534 |  | 214.9475 |  | 192.668 |  | 189.3981
subcool T
massflow
Liquid heater before HEX | Volts (approximate, manual) |  | 140 | 140 | 140 | 140 | 140 | 0 | 140 |  | 170 |  | 165 |  | 165 |  | 153 |  | 153 |  | 165 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 10 |  | 10 |  |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  |  | 153 |  | 153 |  | 153 |  | 146 |  | 0 |  | 0
| temperature after heater (05.23) |  | 35.06 | 35.013 | 35.5 | 35.402 | 35.8 | 23.2 | 36.094 |  | 36.2 |  | 35.7 |  | 35.9 |  | 35.1 |  | 35.6 |  | 35.8 |  | 19.888 |  | 21.868 |  | 22.587 |  | 21.13 |  | 20.965 |  | 19.619 |  | 19.705 |  | 19.484 |  | 19.815 |  | 20.02 |  |  | 20.25 |  | 20.129 |  | 21.667 |  | 20.836 |  |  | 20.328 |  | 21.9 |  | 20.326 |  |  | 35.7 |  | 35.02 |  | 35.711 |  | 35.76 |  | 22.12 |  | 22.11
|  |  | 12:24 Power off detectors leave over lunch | 13:40 power to 50% | 13:58 75% | 14:20 to 100% | 15:44 power to 0% | 4:13:00 PM turn inlet heater off top get TlbHex = 20C | TlbHEX back to 35C to see what stable temps are |  |  | turn power to 50%, first 25%, then 395 then 55% at 15:45 | to 75% power at 16:15 |  |  | start of ramp up to 90% power |  | power to 100% |  | power off - see effect on massflow |  |  |  | increase massflow to 8.8g/s |  | power to 100% | massflow didn’t fall as temps well behaved unlike at TlbEX = 35C | reduce pressure to get massflow = 7.8g/s |  | power off

## power
power supply | Voltage | Current | Power |  |  |  | power |  |  | power
1 | 38.4 | 1.08 | 41.472 |  |  | lower half | 265.652 | 0.50615 | in | 137.406 | 0.51724
2 | 39.6 | 0.64 | 25.344 | --- |  |  |  |  | out | 128.246 | 0.48276
5 | 38.2 | 1.17 | 44.694 | * |  | upper half | 259.197 | 0.49385 | in | 119.991 | 0.46293
6 | 37.7 | 1.16 | 43.732 | * |  |  |  |  | out | 139.206 | 0.53707
9 | 48.8 | 1.05 | 51.24
10 | 48.5 | 1.22 | 59.17
3 | 48.2 | 1.2 | 57.84 | *
7 | 38.2 | 1.05 | 40.11 | n
11 | 38.2 | 1.08 | 41.256 |  |  |  | 12 |  |  |  | 8 |  |  |  | 4
4 | 38.2 | 0.96 | 36.672 |  |  | 0.25683 | 39.066 | 7.751% |  |  | 54.18 | 10.75% |  |  | 36.195 | 7.182%
8 | 38.3 | 1.13 | 43.279 | n
12 | 38.5 | 1.04 | 40.04 |  |  | 0.50982
[7 empty] | 11 |  |  |  | 7 |  |  |  | 3
|  |  | 524.849 | 1.0414 |  | 0.25299 | 41.148 | 8.164% |  |  | 50.74 | 10.07% |  |  | 35.619 | 7.067%
0.99924
supply | V | I | P
1 | 38.3 | 1.08 | 41.364 |  |  | 0.23517 | 36.002 | 7.143% |  |  | 57.64 | 11.44% |  |  | 24.885 | 4.938%
2 | 39.5 | 0.63 | 24.885 |  |  |  | 10 |  |  |  | 6 |  |  |  | 2
3 | 38.3 | 0.93 | 35.619 |  |  | 0.48943
4 | 38.1 | 0.95 | 36.195
5 | 43 | 1.3 | 55.9 |  |  | 0.25425 | 30.88 | 6.127% |  |  | 55.9 | 11.09% |  |  | 41.364 | 8.207%
6 | 44 | 1.31 | 57.64 |  |  |  | 9 |  |  |  | 5 |  |  |  | 1
7 | 43 | 1.18 | 50.74
8 | 43 | 1.26 | 54.18
9 | 38.6 | 0.8 | 30.88
10 | 38.3 | 0.94 | 36.002
11 | 38.1 | 1.08 | 41.148
12 | 38.3 | 1.02 | 39.066
|  |  | 503.619 | 0.99924
554.4
50.4
supply | R | V | 67.6
1 | 35.463 | 48.9622
2 | 62.6984 | 65.1031
3 | 41.1828 | 52.7632
4 | 40.1053 | 52.0684
5 | 33.0769 | 47.2864
6 | 33.5878 | 47.6501
7 | 36.4407 | 49.6325
8 | 34.127 | 48.0311
9 | 48.25 | 57.1113
10 | 40.7447 | 52.4818
11 | 35.2778 | 48.8342
12 | 37.549 | 50.3817
51.6922
data taken
supply | V | I | P | V | I | P | V | I | P | V | I | P | V | I | P |  | V | I | P
1 | 20 | 0.56 | 11.2 | 25 | 0.7 | 17.5 | 30 | 0.84 | 25.2 | 35 | 0.98 | 34.3 | 38 | 1.07 | 40.66 |  | 38 | 1.07 | 40.66
2 | 20 | 0.32 | 6.4 | 25 | 0.4 | 10 | 30 | 0.48 | 14.4 | 35 | 0.57 | 19.95 | 38 | 0.62 | 23.56 |  | 38 | 0.62 | 23.56
3 | 20 | 0.49 | 9.8 | 25 | 0.61 | 15.25 | 30 | 0.73 | 21.9 | 35 | 0.85 | 29.75 | 37.9 | 0.93 | 35.247 |  | 37.9 | 0.93 | 35.247
4 | 20 | 0.5 | 10 | 25 | 0.63 | 15.75 | 30 | 0.75 | 22.5 | 35 | 0.88 | 30.8 | 37.9 | 0.96 | 36.384 |  | 37.9 | 0.96 | 36.384
5 | 20 | 0.6 | 12 | 25 | 0.76 | 19 | 30 | 0.91 | 27.3 | 35 | 1.06 | 37.1 | 38 | 1.16 | 44.08 |  | 43 | 1.32 | 56.76 | *
6 | 20 | 0.61 | 12.2 | 25 | 0.77 | 19.25 | 30 | 0.91 | 27.3 | 35 | 1.07 | 37.45 | 40 | 1.12 | 44.8 | * | 43 | 1.31 | 56.33 | *
7 | 20 | 0.52 | 10.4 | 25 | 0.66 | 16.5 | 30 | 0.8 | 24 | 35 | 0.94 | 32.9 | 38 | 1.02 | 38.76 |  | 43 | 1.19 | 51.17 | *
8 | 20 | 0.57 | 11.4 | 25 | 0.71 | 17.75 | 30 | 0.86 | 25.8 | 35 | 1.01 | 35.35 | 38 | 1.09 | 41.42 |  | 43 | 1.27 | 54.61 | *
9 | 20 | 0.42 | 8.4 | 25 | 0.53 | 13.25 | 30 | 0.63 | 18.9 | 35 | 0.74 | 25.9 | 38 | 0.81 | 30.78 |  | 38 | 0.81 | 30.78
10 | 20 | 0.49 | 9.8 | 25 | 0.66 | 16.5 | 30 | 0.75 | 22.5 | 35 | 0.87 | 30.45 | 38 | 0.94 | 35.72 |  | 38 | 0.94 | 35.72
11 | 20 | 0.57 | 11.4 | 25 | 0.71 | 17.75 | 30 | 0.85 | 25.5 | 35 | 0.99 | 34.65 | 38 | 1.08 | 41.04 |  | 38 | 1.08 | 41.04
12 | 20 | 0.53 | 10.6 | 25 | 0.67 | 16.75 | 30 | 0.8 | 24 | 35 | 0.94 | 32.9 | 38 | 1.02 | 38.76 |  | 38 | 1.02 | 38.76
|  |  | 123.6 |  |  | 195.25 |  |  | 279.3 |  |  | 381.5 |  |  | 451.211 |  |  |  | 501.021
|  |  | 24.52% |  |  | 38.74% |  |  | 55.42% |  |  | 75.69% |  |  | 89.53% |  |  |  | 99.41%
*
= use of extra power supply in series to main supply. Overall voltage measured with volt meter

## eff_fun_TlbHEX
Date / Time | date/time | 8.10. / 18:36 | 16:24 | 16:54 | 17:21
mass flow | by Danfoss | 8.074 | 8.428 | 8.496
| by Volume / time | 7.54 | 7.79 | 7.81 | 7.81
Characteristic values: | Power on staves | 0% | 99.31% | 100.9% | 100.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Inlet temp into HEX | 34.5 | 20.191 | 30.3315 | 35.373 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Massflow | 7.54 | 7.79 | 7.81 | 7.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pressures | before capillary (manometer) | 16.7 | 16.6 | 18.5 | 19.1
directly after capillariess | PlaCAP 1&2(manometer) | 1.78
differential accorss caps | DiffPCAP (00.06) | 14.772 | 14.524 | 16.426 | 17.207
after capillaries | PlaCAP (00.01) | n/a | 1.981 | 1.913 | 1.85
| differential across HEX liquid (00.04) | 0.104 | 0.123 | 0.124 | 0.105
Cap temperatures | before cap0 (05.25) | -11.94 | -10.13 | 4.839 | 10.441
| before cap1 (05.18) | -8.923 | -6.259 | 7.402 | 13.126
| average TlbCAP |  | -8.1945 | 6.1205 | 11.7835
| after cap0 (05.21) | -10.14 | -9.381 | 5.543 | 10.946
| after cap1 (05.16) | -7.427 | -9.601 | 3.235 | 7.238
HEX efficiency/temps | TlbHEX (05.24) | 35 | 20.219 | 30.369 | 35.4
| TlbHEX (05.26) | 34 | 20.163 | 30.294 | 35.346
| average TlbHEX | 34.5 | 20.191 | 30.3315 | 35.373 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| TlaHEX (05.22) | -13.09
| TlaHEX (05.07) | -10.77 | -12.15 | 2.637 | 8.854
| average TlaHEX | -11.93 | -12.15 | 2.637 | 8.854 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| TvbHEX (05.19) | -25.02 | -22.2 | -24.13 | -24.06
| TvaHEX (05.18) | -25.68 | -8.048 | 6.395 | 13.297
| HEX efficiency | 0.78034 | 0.71565 | 0.50973 | 0.44665 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Other Pressures | differential across HEX vapor (00.03) |  | 0.145 | 0.137 | 0.142
| Pres. drop over inlet tube (00.05) | 0.143 | 0.146 | 0.175 | 0.178
| Pres. Before HEX (man) | 16.75 | 16.75 | 18.4 | 19.2
| Pvafter outlet pipe (00.00) | 1.606 | 1.762 | 1.67 | 1.604
| pressure before BPR (00.02) | 1.397 | 1.472 | 1.35 | 1.266
Detector heating | Volts | 0 | 182 | 183 | 183
| Current | 0 | 2.75 | 2.78 | 2.78
| Power on detector structure [W] | 0 | 500.5 | 508.74 | 508.74
nominal power = 504W | % | 0 | 0.99306 | 1.0094 | 1.0094
Power from I^2R (R=66.2)
Vapor heater after HEX | Volts | 90 | 100 | 100 | 100
| Current |  | pid | pid | pid
Power P=VI
Power on heater | P=V2/R, R=14 - need tocheck
| Temp after vapor heater (05.21) | 25
VQ inlet
VQ outlet
| Tlbmass flow meter (05.20) | 30 | 22.44 | 22.846 | 21.437
| temp in massflow meter (manual) | 20.8 | 19.02 | 19.45 | ----
Hliq_sat
Hvap_sat
Hwe_cap
Liquid heater before HEX | Volts (approximate, manual) | 130 | 0 | 190 | 190
| temperature after heater (05.23) | 30.37 | 20.567 | 31.61 | 36.601
|  |  | power to 100% (16:21) | 16:36 increase pressure toget to 7.8g/s | 17:01 increase pressure slightly

## eff_fun_power
Date / Time | date/time | 15:30 | 16:04 | 16:13 | 16:24 | 20/09/2004 | 12:21 | 15:10 | 16:02 | 16:54 | 15:50 | 16:27 | 17:37 | 17:51 | 27/09/2004 | 10:20
mass flow | by Danfoss | 8.453 | 8.457 | 8.467 | 8.428 | 8.409 | 8.377 | 8.398 | 8.39 | 8.496 | 23/09/2004 |  |  | 9.28
| by Volume / time | 7.78 | 7.8 | 7.82 | 7.79 | 7.84 | 7.76 | 7.77 | 7.71 | 7.81 | 8.36 | 7.97 | 7.8 | 8.46 |  | 7.79
Characteristic values: | Power on staves | 0% | 53.04% | 75.77% | 99.31% | 0% | 52.9% | 75% | 88.73% | 100.9% | 0% | 90.96% | 100.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Inlet temp into HEX | 19.64 | 20.02 | 20.0765 | 20.191 | 29.925 | 30.071 | 30.5815 | 30.769 | 30.3315 | 34.6995 | 34.744 | 35.513 | 35.4965 | #DIV/0! | 34.98 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Massflow | 7.78 | 7.8 | 7.82 | 7.79 | 7.84 | 7.76 | 7.77 | 7.71 | 7.81 | 8.36 | 7.97 | 7.8 | 8.46 | 0 | 7.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pressures | before capillary (manometer) | 16.4 | 16.65 | 16.6 | 16.6 | 16.4 | 16.4 | 16.5 | 17 | 18.5 | 18.6 | 18.65 | 19.1 | 19.2 |  | 15.2
directly after capillariess | PlaCAP 1&2(manometer)
differential accorss caps | DiffPCAP (00.06) | 14.457 | 14.559 | 14.504 | 14.524 | 14.536 | 14.409 | 14.486 | 14.952 | 16.426 | 16.667 | 16.712 | 17.162 | 17.195 |  | 13.407
after capillaries | PlaCAP (00.01) | 1.89 | 1.989 | 1.999 | 1.981 | 1.931 | 2.004 | 1.967 | 1.89 | 1.913 | 1.903 | 1.876 | 1.841 | 1.893 |  | 1.848
| differential across HEX liquid (00.04) | 0.13 | 0.131 | 0.127 | 0.123 | 0.12 | 0.102 | 0.126 | 0.125 | 0.124 | 0.149 | 0.136 | 0.126 | 0.142 |  | 0.127
Cap temperatures | before cap0 (05.25) | -14.09 | -10.97 | -10.77 | -10.13 | -8.737 | -8.262 | -8.569 | -5.621 | 4.839 | -7.216 | 5.692 | 10.913 | -7.16 |  | -9.464
| before cap1 (05.18) | -8.711 | -7.48 | -7.281 | -6.259 | -5.88 | -4.986 | -4.561 | -0.961 | 7.402 | -2.337 | 7.822 | 13.586 | -2.051 |  | -6.756
| average TlbCAP | -11.4005 | -9.225 | -9.0255 | -8.1945 | -7.3085 | -6.624 | -6.565 | -3.291 | 6.1205 | -4.7765 | 6.757 | 12.2495 | -4.6055 | #DIV/0! | -8.11 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| after cap0 (05.21) | -12.14 | -10.65 | -10.48 | -9.381 | -8.963 | -7.781 | -7.574 | -3.791 | 5.543 | -5.03 | 5.974 | 11.125 | -4.974 |  | -5.85
| after cap1 (05.16) | -13.25 | -10.33 | -10.14 | -9.601 | -8.656 | -8.165 | -8.489 | -5.738 | 3.235 | -7.147 | 4.048 | 7.479 | -7.119 |  | -8.003
HEX efficiency/temps | TlbHEX (05.24) | 19.678 | 20.057 | 20.113 | 20.219 | 29.961 | 30.112 | 30.616 | 30.806 | 30.369 | 34.729 | 34.773 | 35.54 | 35.535 |  | 35.025
| TlbHEX (05.26) | 19.602 | 19.983 | 20.04 | 20.163 | 29.889 | 30.03 | 30.547 | 30.732 | 30.294 | 34.67 | 34.715 | 35.486 | 35.458 |  | 34.935
| average TlbHEX | 19.64 | 20.02 | 20.0765 | 20.191 | 29.925 | 30.071 | 30.5815 | 30.769 | 30.3315 | 34.6995 | 34.744 | 35.513 | 35.4965 | #DIV/0! | 34.98 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| TlaHEX (05.22) | [14 empty] | -11.2
| TlaHEX (05.07) | -14.76 | -13.33 | -13.15 | -12.15 | -11.36 | -10.56 | -10.405 | -7.237 | 2.637 | -7.488 | 3.089 | 9.156 | -7.789 |  | -8.808
| average TlaHEX | -14.76 | -13.33 | -13.15 | -12.15 | -11.36 | -10.56 | -10.405 | -7.237 | 2.637 | -7.488 | 3.089 | 9.156 | -7.789 | #DIV/0! | -10.004 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| TvbHEX (05.19) | -24.33 | -22.15 | -22.21 | -22.2 | -23.28 | -21.92 | -22.35 | -23.33 | -24.13 | -22.57 | -23.79 | -24.07 | -23.36 |  | -22.34
| TvaHEX (05.18) | -23.8 | -23.13 | -23.57 | -8.048 | -23.21 | -22.54 | -11.94 | 0.565 | 6.395 | -23.69 | 5.6 | 13.695 | -24.12 |  | 1.703
| HEX efficiency | 0.77061 | 0.77522 | 0.75384 | 0.71565 | 0.7656 | 0.7656 | 0.75092 | 0.69393 | 0.50973 | 0.7187 | 0.53886 | 0.44288 | 0.72753 | #DIV/0! | 0.7627 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Other Pressures | differential across HEX vapor (00.03) | 0.061 | 0.106 | 0.133 | 0.145 | 0.065 | 0.115 | 0.132 | 0.145 | 0.137 | 0.94 | 0.15 | 0.14 | 0.111 |  | 0.079
| Pres. drop over inlet tube (00.05) | 0.145 | 0.173 | 0.152 | 0.146 | 0.123 | 0.12 | 0.181 | 0.152 | 0.175 | 0.174 | 0.161 | 0.155 | 0.166 |  | 0.117
| Pres. Before HEX (man) | 16.5 | 16.75 | 16.75 | 16.75 | 16.5 | 16.5 | 16.6 | 16.9 | 18.4 | 18.7 | 18.75 | 19.2 | 19.3 |  | 15.4
| Pvafter outlet pipe (00.00) | 1.761 | 1.791 | 1.758 | 1.762 | 1.792 | 1.773 | 1.712 | 1.635 | 1.67 | 1.748 | 1.618 | 1.593 | 1.718 |  | 1.684
| pressure before BPR (00.02) | 1.483 | 1.501 | 1.464 | 1.472 | 1.539 | 1.512 | 1.431 | 1.333 | 1.35 | 1.415 | 1.276 | 1.266 | 1.376 |  | 1.36
Detector heating | Volts | 0 | 133 | 156.5 | 182 | 0 | 132 | 157.5 | 172 | 183 | 0 | 173 | 183 | 0 |  | 0
| Current | 0 | 2.01 | 2.44 | 2.75 | 0 | 2.02 | 2.4 | 2.6 | 2.78 | 0 | 2.65 | 2.78 | 0 |  | 0
| Power on detector structure [W] | 0 | 267.33 | 381.86 | 500.5 | 0 | 266.64 | 378 | 447.2 | 508.74 | 0 | 458.45 | 508.74 | 0 |  | 0
nominal power = 504W | % | 0 | 0.53042 | 0.75766 | 0.99306 | 0 | 0.52905 | 0.75 | 0.8873 | 1.0094 | 0 | 0.90962 | 1.0094 | 0 |  | 0
Power from I^2R (R=66.2)
Vapor heater after HEX | Volts | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100
| Current | pid | pid | pid | pid | pid | pid | pid | pid | pid | pid | pid | pid | pid |  | pid
Power P=VI
Power on heater | P=V2/R, R=14 - need tocheck
Temp after vapor heater (05.21)
VQ inlet
VQ outlet
| Tlbmass flow meter (05.20) | 21.713 | 22.099 | 22.238 | 22.44 | 20.424 | 20.646 | 22.1 | 22.554 | 22.846 | 20.668 | 21.117 | 21.46 | 21.527 |  | 17.7
| temp in massflow meter (manual) | 18.74 | 18.98 | 19 | 19.02 | 18.02 | 18.08 | 18.62 | 18.82 | 19.45 | ---- | ---- | ---- | 25 |  | ----
Hliq_sat
Hvap_sat
Hwe_cap
Liquid heater before HEX | Volts (approximate, manual) | 0 | 0 | 0 | 0 | 200 | 200 | 200 | 200 | 190 | 200 | 190 | 190 | 200 |  | 200
| temperature after heater (05.23) | 20.169 | 20.471 | 20.516 | 20.567 | 31.503 | 31.638 | 32.11 | 32.223 | 31.61 | 36.117 | 35.976 | 36.657 | 36.849 |  | 36.545
|  |  | increase prressure slightly at 15:58 | power to 75% (16:08) | power to 100% (16:21) |  | 12:27 det power off, pressure down to 15bara - lunch | 14:47 back after lunch+spine stuff, back to 30C and 16.5bara pressure, 50% power on det | 15:52 increase pressure slightly | 16:36 increase pressure toget to 7.8g/s | restarted system on 23/09/2004 | 16:05 power on to 90% | left alone for 10 minutes to see if flat | 17:37 turn off det power and measure massflow | cut capillaries by 30cm - now 2.4m |  | increased pressure to give higher massflow, want 8.5g/s
massflow meter put back into circuit after all other measuremnets were taken

## Sheet3
| 2004-03-12 | TlaDanfoss | Pressure | Danfoss | TinDanfoss | Danfoss ave | T ave | Volume | Diff | Diff %
wish to study:
A - done | difference in Danfoss with volume meter as T in Danfoss changes | 19.2 to 18.2 | 11.72 | 8.056 | 16.02 | 8.0405 | 15.995 | 7.39 | 0.6505 | 8.09%
| do for about 8g/s as measured by volume meter |  |  | 8.025 | 15.97
B - done | pressure drops for massflow = 7.8g/s
| TlbHEX = 20C | 20 | 13.75 | 8.91 | 17.76 | 8.91 | 17.825 | 8.15 | 0.76 | 8.53%
C - doing | find pressure drop for 100% power and TlbHEx = 20C |  |  | 8.91 | 17.89
measured with pressures to give massflow 7.8g/s TlbHEX = 35C
D - done | find minimum massflow for TlbHEX = 20C | 20 | 12.75 | 8.509 | 17.77 | 8.4995 | 17.725 | 7.75 | 0.7495 | 8.818%
E | for fixed massflow (7.8g/s) and full power |  |  | 8.49 | 17.68
change vq by changing TlbHEX and prssures
| plot DP fun(vq) | 20 | 15.25 | 9.086 | 17.96 | 9.11 | 18.05 | 8.26 | 0.85 | 9.33%
|  |  |  | 9.134 | 18.14
D - done 6.8g/s okay, HEX 50% eff,drop 0.5bara and fails | min massflow for TlbHEX = 20C | 20 | 12.5 | 8.371 | 17.72 | 8.3655 | 17.705 | 7.65 | 0.7155 | 8.553%
F - done 10% okay, 15% bad | extra power possible for TlbHEX = 20C and m=7.8g.s |  |  | 8.36 | 17.69
C | extra massflow for TlbHEX =35 to 20C, 100% power, 7.8g/s at 35C
|  | 22.48 | 12.4 | 8.319 | 20.9 | 8.3445 | 21.075 | 7.62 | 0.7245 | 8.682%
|  |  |  | 8.37 | 21.25
y = 0.2548x + 4.4747
x = (y-4.4747)/0.2548
x = pressure
y = massflow
|  |  | massflow | pressure
|  |  | 7.8 | 13.0506
|  |  | 8.8 | 16.9753