Endcap tests

The geometry tested was the -45deg and 45deg orientations. The HEX was not tested in the horizontal plane.

Vapour in

45

HEX out of page

x

z

+45 deg geometry

for the CERN prototype these results were found:

Table 1

| Date | 1/8/2004 | 2/8/2004 |
| --- | --- | --- |
| date/time |  | 18:44 |
| Mass-flow by Danfoss | 5.83572 | 5.71632 |
| Mass-flow by volume | 5.50 | 5.42 |
| Power on staves | 99.4% | 99.4% |
| Inlet temp into HEX | 34.34534 | 35.42596 |
| Orientation | -45deg | +45deg |
| P before capillaries (manometer) | 14.2 | 14.25 |
| P after capillaries (manometer) | 1.74 | 1.73 |
| DP over capillaries (00.06) | 12.42114 | 12.5083 |
| P after capillaries (00.01) | 1.75642 | 1.70706 |
| DP over HEX liquid (00.03) | 0.98544 | 0.90102 |
| T before cap1&2 (05.16) | -13.384 | -5.4828 |
| T before cap3 (05.17) | -13.7208 | -5.7185 |
| T after cap1&2 (05.19) | -12.8089 | -4.96808 |
| T after cap3 (05.25) | -13.1887 | -5.0091 |
| T liquid before HEX (05.24) | 34.34534 | 35.42596 |
| T liquid after HEX | -15.07154 | -6.52863 |
| T vapor before HEX (05.18) | -24.9248 | -25.1745 |
| T vapor after HEX (05.26) | 16.91754 | 19.1953 |
| HEX efficiency | 0.83 | 0.69 |
| DP over inlet pipe (00.05) | 0.09036 | 0.0836 |

For the QM-1 HEX these results were found at the highest power that we ran at:

Table 2

| Date / Time | date/time | 15:48 | 20:05 |
| --- | --- | --- | --- |
| mass flow | by Danfoss | 6.55 | 6.36 |
|  | Temp in flowmeter | 16.48 | 16.32 |
|  | by Volume / time | 6.02 | 5.84 |
|  |  | +45deg, vapour end down | -45deg, vapour end up |
| Characteristic values: | Power on staves | 101.7% | 97.5% |
|  | Inlet temp into HEX | 32.79 | 34.57 |
|  | Massflow | 6.02 | 5.84 |
|  |  | Dan/Vol = 1.088 | Dan/Vol = 1.089 |
| Pressures | Keller | 12.95 | 13.08 |
| directly after capillaries | ABS press 00.01 | 1.74 | 1.73 |
| differential across caps | DiffPCAP (00.06) | 11.08 | 11.33 |
| Cap temperatures | before cap (MoTe06 06:12) | -4.37 | -8.07 |
|  | before cap (MoTe03 06.09) | -5.26 | -9.34 |
|  | after cap (MoTe05 06.11) | -16.44 | -16.93 |
|  | after cap (MoTe04 06.10) | -17.44 | -15.89 |
| HEX efficiency/temps | TlbHEX (MoTe02 06.04) | 32.79 | 34.57 |
|  | TlaHEX (CaTe03 06.06) | -5.3 | -9.08 |
|  | TvbHEX (PiTe23 06.05) | -23.63 | -24.63 |
|  | TvaHEX (CaTe02 06.03) | 7.67 | 12.16 |
|  | HEX efficiency | 0.67 | 0.75 |
|  | Temp after detectors (CaTe04 06.07) | -20.64 | -21.69 |
| Other Pressures | DiffP caps (InPr21 00.06) | 11.08 | 11.33 |
|  | diffP across HEX liquid (BaPr16 00.13) | 1.18 | 1.12 |
|  | DiffP on-cylind (InPr03 00.04) | 0.14 | 0.13 |
|  | DiffP Hex vapour (BaPr15 00.03) | 0.06 | 0.06 |
|  | Press BPR (BaPR01 00.02) | 1.31 | 1.28 |
| Detector heating | Volts | 152.8 | 149.3 |
|  | Current | 2.306 | 2.262 |
|  | Power on detector structure [W] | 352.3568 | 337.7166 |
|  | % | 1.017 | 0.975 |
|  | Power from I^2R (R=66.2) | 1.016 | 0.978 |
| Vapor heater after HEX | Control | pid | pid |
|  | % of full power | 9% | 7% |
|  | Temp after vapour heater (PiT12 05.17) | 23 | 22 |
| VQ inlet |  |  |  |
| VQ outlet |  |  |  |
| Hliq_sat |  |  |  |
| Hvap_sat |  |  |  |
| Hwe_cap |  |  |  |
| Liquid heater before HEX | Volts (approximate, manual) | 215 | 215 |
|  | temperature before filter (06.00) | 33.94 | 35.27 |

For the QM-1 version the HEX would appear to be running at a colder temperature with the -45deg orientation as with the CERN prototype, BUT with a lower massflow, the difference is 3% (0.18g/s). This is not at all obvious from the fact that the input pressures to the capillaries are the same. Looking at 75% power we see:

Table 2

| Date / Time | date/time | 14:50 | 06:14 |
| --- | --- | --- | --- |
| mass flow | by Danfoss | 6.68 | 6.6 |
|  | Temp in flowmeter | 16.52 | 16.43 |
|  | by Volume / time | 6.14 | 6.11 |
|  |  | +45deg | -45deg |
| Characteristic values: | Power on staves | 76.3% | 76.2% |
|  | Inlet temp into HEX | 31.6 | 33.61 |
|  | Massflow | 6.14 | 6.11 |
|  |  | Dan/Vol = 1.088 | Dan/Vol = 1.08 |
| Pressures | Keller | 13 | 12.97 |
| directly after capillaries | ABS press 00.01 | 1.71 | 1.68 |
| differential across caps | DiffPCAP (00.06) | 11.15 | 11.25 |
| Cap temperatures | before cap (MoTe06 06:12) | -10.06 | -18.77 |
|  | before cap (MoTe03 06.09) | -10.99 | -20.13 |
|  | after cap (MoTe05 06.11) | -20.43 | -22.21 |
|  | after cap (MoTe04 06.10) | -21.13 | -21.43 |
| HEX efficiency/temps | TlbHEX (MoTe02 06.04) | 31.6 | 33.61 |
|  | TlaHEX (CaTe03 06.06) | -11 | -21.12 |
|  | TvbHEX (PiTe23 06.05) | -23.77 | -24.7 |
|  | TvaHEX (CaTe02 06.03) | -25.05 | -25.37 |
|  | HEX efficiency | 0.77 | 0.95 |
|  | Temp after detectors (CaTe04 06.07) | -21.03 | -21.82 |
| Other Pressures | DiffP caps (InPr21 00.06) | 11.16 | 11.25 |
|  | diffP across HEX liquid (BaPr16 00.13) | 1.22 | 1.22 |
|  | DiffP on-cylind (InPr03 00.04) | 0.12 | 0.11 |
|  | DiffP Hex vapour (BaPr15 00.03) | 0.05 | 0.05 |
|  | Press BPR (BaPR01 00.02) | 1.33 | 1.32 |
| Detector heating | Volts | 132.1 | 131.2 |
|  | Current | 2.001 | 2.012 |
|  | Power on detector structure [W] | 264.3321 | 263.9744 |
|  | % | 0.76 | 0.76 |
|  | Power from I^2R (R=66.2) | 0.76 | 0.77 |
| Vapor heater after HEX | Volts | pid | pid |
|  | Current | 21% |  |
|  | Power P=VI |  |  |
| Power on heater | P=V2/R, R=14 - need tocheck |  |  |
|  | Temp after vapor heater (PiT12 05.17) | 22.08 | 22 |
| VQ inlet |  |  |  |
| VQ outlet |  |  |  |
| Hliq_sat |  |  |  |
| Hvap_sat |  |  |  |
| Hwe_cap |  |  |  |
| Liquid heater before HEX | Volts (approximate, manual) | 215 | 215 |
|  | temperature before filter (06.00) | 33.73 | 34.62 |

And again the temperatures before the capillaries are lower for the -45deg orientation, again the massflow is slightly lower or the same, but the difference is now only 0.5% or 0.03g/s!

There is also a difference between the two orientations in the pressures that are measured. For the -45deg set-up the pressure before the capillaries, (PlbCap), is given by the sum of the differential pressure across the capillaries, (DPCap), and the pressure of the fluid after the capillaries, (PvaCap). While for the +45deg orientation the PlbCap is greater than the sum of DPCap and PvaCap by 130-140mbar.

Noted that the position of the keller and huba diff pressure sensors are at different points relative to the input of the capillary for the two set-ups. The pressure measured at the sensor is given by the real pressure at the capillary input plus, (or minus), the pressure due to the head of liquid above (below) the sensor between the capillary input and the sensor.

The measurements at deg were repeated with the keller and the huba sensor at the same height as the input of the capillaries.

Also the effect on the measured pressure caused by changing the position of the keller was noted.

Lowering the Keller to a position 30cm below the capillary input increased the measured pressure by 40mbar, due to the extra head of liquid. The liquid pressure is 13bara and temperature is -20C. From P=gh =40mbar the liquid density can be found to be 1360kg/m3. The quoted saturation density at 40C and 13bara is 1226kg/m3 and is 1268kg/m3 at 34C and 11bara and 1561kg/m-3 at -24C and 1.739bara. It would appear that the density of the liquid is closer to that for 13bara than for 1.729bara.If P changed by 50mbar then the density would be 1700kg/m-3 which is higher than the cold conditions. The change in measured pressure was between 40 and 50mbar.

Comparing the data with the Keller and Huba pressure sensors at the capillary inlet and before when they were at difference levels for the +45deg orientation. Note the keller was 30cm below the capillaries in the older data which is a difference in the real PlbCap and the measured of 40-50mbar. This means that the real PlbCap is 12.91 for the old data and 13.01 for the new data. The TlbCaps is about the same for both runs. The Pevap is the same as is the measured DPlCap, but if you correct for the change in height of the huba sensor then the Real Diff Pressure is 11.06 for the new data and 11.12 for the old data. This is not consistent with the lower input pressure. The diff pressure should actually be 11.17-0.2 = 10.93

| Date / Time | date/time | 19:20 | 15:48 |
| --- | --- | --- | --- |
| mass flow | by Danfoss | 6.58 | 6.55 |
|  | Temp in flowmeter | 16.24 | 16.48 |
|  | by Volume / time | 5.99 | 6.02 |
|  |  | +45deg, now with the keller and Huba P1 at capillary input level | Incorrect level |
| Characteristic values: | Power on staves | 98.8% | 101.7% |
|  | Inlet temp into HEX | 34.71 | 32.79 |
|  | Massflow | 5.99 | 6.02 |
|  |  | D/V=1.098 | Dan/Vol = 1.088 |
| Pressures | Keller | 13.01 | 12.95 |
|  | Real PlbCAP | 13.01 | 12.91 |
| directly after capillaries | ABS press 00.01 | 1.74 | 1.74 |
| differential across caps | DiffPCAP (00.06) | 11.06 | 11.08 |
|  | Real DiffCap | 11.06 | 11.12 |
| Cap temperatures | before cap (MoTe06 06:12) | -4.52 | -4.37 |
|  | before cap (MoTe03 06.09) | -4.65 | -5.26 |
|  | Average TlbCap | -4.585 | -4.815 |
|  | after cap (MoTe05 06.11) | -16.44 | -16.44 |
|  | after cap (MoTe04 06.10) | -17.25 | -17.44 |
|  | Average TlaCap | -16.845 | -16.94 |
| HEX efficiency/temps | TlbHEX (MoTe02 06.04) | 34.71 | 32.79 |
|  | TlaHEX (CaTe03 06.06) | -7.58 | -5.3 |
|  | TvbHEX (PiTe23 06.05) | -14.63 | -23.63 |
|  | TvaHEX (CaTe02 06.03) | 5.31 | 7.67 |
|  | HEX efficiency | 0.72 | 0.67 |
|  | Temp after detectors (CaTe04 06.07) | -20.68 | -20.64 |
| Other Pressures | DiffP caps (InPr21 00.06) | 11.06 | 11.08 |
|  | diffP across HEX liquid (BaPr16 00.13) | 1.18 | 1.18 |
|  | DiffP on-cylind (InPr03 00.04) | 0.12 | 0.14 |
|  | DiffP Hex vapour (BaPr15 00.03) | 0.06 | 0.06 |
|  | Press BPR (BaPR01 00.02) | 1.31 | 1.31 |
| Detector heating | Volts | 150.5 | 152.8 |
|  | Current | 2.274 | 2.306 |
|  | Power on detector structure [W] | 342.237 | 352.3568 |
|  | % | 0.99 | 1.017 |
|  | Power from I^2R (R=66.2) | 0.99 | 1.016 |
| Vapor heater after HEX | Volts | pid | pid |
|  | Current | 10% | 9% |
|  | Power P=VI |  |  |
| Power on heater | P=V2/R, R=14 - need tocheck |  |  |
|  | Temp after vapor heater (PiT12 05.17) | 22.7 | 23 |
| VQ inlet |  | -3% | 7% |
| VQ outlet |  | 56% | 64% |
| Hliq_sat |  | 184 | 174 |
| Hvap_sat |  | 282 | 277 |
| Hdiff_sat |  | 98 | 102 |
| Hliq_end_cap |  | 182 | 182 |
| Liquid heater before HEX | Volts (approximate, manual) | 220 | 215 |
|  | temperature before filter (06.00) | 34.64 | 33.94 |