## Sheet1
Date / Time | date/time | 24.6.04 / 12:30 | 2005-04-03 | 16:09 |  | 16:30 |  | 16:36 | 16:42 | 16/03/2005 | 14:23 | 15:26 | 16:35 |  | 17:06 | 17:26 | 17:31 turn system off |  | 22/03/2005 |  | 10:14 | 10:45 | 11:05 | 11:25 | 11:45 | cut capillaries to give a massflow of 5.77g/s | 23/03/2005 | 11:41 | 12:04 | 13:25 | 13:53 | 14:24 |  | 14:49 | 15:13 | 15:30 |  | 18:05 | 438:14 | 18:40 | 19:10 | 19:40 | 20:05 | unstable!! | 29/03/2005 | 14:08 | 14:32 | 14:50 | 15:13 | 15:24 | 15:48 | 16:15 | 31/03/2005 | 18:49 | 19:20 | 19:36 | 19:49 | 20:08 |  |  | 21/04/2005 | 13:48 | 14:17-14:27 | 14:50-15:00 | 15:38-15:48 | 16:01-16:11 | 16:28-16:38 | 17:05-17:14 | 17:33-17:41 | 17:48-17:54 | 18:01-18:08
mass flow | by Danfoss | 5.98 | All tests with vapour end up | 6.15 |  | 6.09 |  | 6.06 | 6.05 |  | system on | 5.99 | 5.8 |  | n/a | increasig TlbHEX causes thermal run away at 28C! |  |  |  | 09:00 system on | 5.77 to 5.75 | 6.03 to 6.025 | 6.062 - 6.055 | 6.086 to 6.1 | 5.75 | from CERN prototype should have been 5.7g/s!!! | 10:30 system on | 6.21 | 6.36 | 6.58 | 6.6 | 6.04 to 5.98 |  | 6.34 | 6.619 | 6.58 |  | 6.28 | 6.6 | 6.52 | 6.429 | 6.39 | 6.36 |  | 13:30 | 6.54 | 6.7 | 6.68 | 6.6 | 6.59 | 6.55 | 6.73 | moved the keller so that it is level with the capillary inlet. Moved DP over cap so P1 is level with the capillary input | 6.57 | 6.58 | 6.49 | 6.44 | 6.69 |  |  | tests below | 6.48 | 6.527 | 6.649 | 6 | 5.935 | 6.745 | 5.997 | 6.764 | 6.05 | 6.8
| Temp in flowmeter |  | +45deg | 13.4 |  | 14.2 |  | 14.25 | 14.27 |  |  | 14.38 | 14.95 |  | n/a |  |  |  |  | plan: | 15.37 | 15.54 | 15.6 | 15.64 | 15.49 |  |  | 15.9 | 16.03 | 16.3 | 16.36 | 16.04 |  | 16.16 | 16.4 | 16.46 |  | 16.25 | 16.43 | 16.45 | 16.4 | 16.37 | 16.32 |  | system on | 16.24 | 16.47 | 16.52 | 16.5 | 16.44 | 16.48 | 16.54 |  | 16.2 | 16.24 | 16.2 | 16.2 | 16.29 |  |  |  | 15.87 | 16.29 | 16.5 | 16.1 | 16.05 | 16.57 | 16.17 | 16.7 | 16.35 | 16.5
| by Volume / time | 5.91 | [9 empty] | 5.32 | 5.33 |  | 5.33 |  |  |  |  | take TlbHEX 35C | 5.33 | 5.52 | 5.56 | 5.65 | 5.25 |  |  | 5.8 | 5.85 | 6.1 | 6.09 | 5.54 |  | 5.91 | 6.14 | 6.06 |  | 5.81 | 6.11 | 6.02 | 5.91 | 5.82 | 5.84 |  | swoped orientation | 6.01 | 6.19 | 6.14 | 6.1 | 6.07 | 6.02 | 6.23 |  | 6.03 | 5.99 | 5.9 | 5.8 | 6.16 |  |  |  | 5.99 | 5.99 | 6.13 | 5.52 | 5.53 | 6.22 | 5.58 | 6.2 | 5.61 | 6.23
[21 empty] | (5.21 to 5.45 taken over 7.5mins) | (5.48 to 5.56 over 8.5mins) | (5.48 - 5.64 ave over 8mis) | (no change in pressure, ave over 7.5mins) |  |  |  | range = 5.6 to 6 ave over 8 mins |  | 6.1 to 6.18g/s ave 11:44mins | (6.05 to 6.13 ave over 8:22mins) |  |  | (5.83 to 5.99 ave over 8mins) | (5.94 to 6.35 ave over 10mins) | (5.86 to 6.27, ave over 6:30mins) |  | (5.65 rto 5.97 ave 4mins) |  | no variation in Vol | no variation in Vol | no variation in Vol |  |  | vapour end down | (ave 4:30 mins) | (6.11 to 6.27, ave over 8:30mins) | (6.10 to 6.18, ave over 11:00mins) | (ave over 12mins) |  | (ave over 12mins) | (ave over 9mins) |  | (5.91 to 6.15g/s) |  |  |  | (range 6.04 to 6.28) |  |  | % above 5.77g/s | 3.813% | 3.813% | 6.239% | -4.333% | -4.159% | 7.799% | -3.293% | 7.452% | -2.773% | 7.972%
Characteristic values: | Power on staves | 100.2% |  | 0% |  | 101.6% |  | 101.6% | 101.6% |  |  | 0% | 101.8% |  | 101.9% |  |  |  |  | see max power and massflow, with Vol and Danfoss | 0% | 24.46% | 50.4% | 73.84% | 90.18% |  |  | 0% | 25.85% | 51.76% | 75.69% | 100.5% | system fails to hold 100% power! | 0% | 0% | 0% |  | 0% | 76.18% | 84.52% | 89.74% | 95.19% | 97.47% | 100.3% | -45deg | 0% | 51.67% | 76.29% | 100.1% | 0.005772% | 101.7% | 0% |  | 0% | 98.77% | 98.81% | 98.03% | 0% |  |  |  | 0% | 100.2% | 100.5% | 100.3% | 102.2% | 102.1% | 101.3% | 101.9% | 99.95% | 0%
| Inlet temp into HEX | 21 |  | 18.2 |  | 19.47 |  | 23.33 | 23.33 |  |  | 24.03 | 26 |  | 25.94 |  |  |  |  | then pump down and cut caps to give correct massflow | 35 | 33.75 | 33.65 | 34.94 | 35 |  |  | 33.95 | 33.56 | 33.44 | 33.71 | 34.47 |  | 34.54 | 20.38 | 20.42 |  | 33.88 | 33.61 | 33.88 | 34.17 | 34.37 | 34.57 | 0 |  | 30.83 | 30.79 | 31.6 | 33.03 | 30.89 | 32.79 | 19.03 |  | 34.59 | 34.71 | 34.94 | 34.98 | 20.85 |  |  |  | 34.63 | 34.79 | 29.85 | 30.12 | 29.97 | 24.8 | 24.72 | 20.54 | 20.3 | 20.07
| Massflow | 5.98 |  | 6.15 |  | 6.09 |  | 6.06 | 6.05 |  |  | 5.32 | 5.33 |  | 5.33 | [5 empty] | 5.33 | 5.52 | 5.56 | 5.65 | 5.25 |  |  | 5.8 | 5.85 | 6.1 | 6.09 | 5.54 |  | 5.91 | 6.14 | 6.06 |  | 5.81 | 6.11 | 6.02 | 5.91 | 5.82 | 5.84 | 0 |  | 6.01 | 6.19 | 6.14 | 6.1 | 6.07 | 6.02 | 6.23 |  | 6.03 | 5.99 | 5.9 | 5.8 | 6.16 |  |  |  | 5.99 | 5.99 | 6.13 | 5.52 | 5.53 | 6.22 | 5.58 | 6.2 | 5.61 | 6.23
[21 empty] | diff Danfoss/Vol = 8% high | Dan/Vol = 9% high | Dan/Vol = 9% high | Dan/Vol = 8% high |  |  |  | Dan/Vol = 1.071 | Dan/Vol = 1.087 | Dan/Vol = 1.079 | Dan/Vol = 1.084 |  |  | Dan/Vol = 1.073 | Dan/Vol = 1.078 | Dan/Vol = 1.086 | [9 empty] | Dan/Vol = 1.0849 | Dan/Vol = 1.0824 | Dan/Vol = 1.0879 | Dan/Vol = 1.082 | Dan/Vol = 1.0857 | Dan/Vol = 1.0880 | Dan/Vol = 1.0803 | [9 empty] | 1.0818 | 1.0896 | 1.0847 | 1.087 | 1.0732 | 1.0844 | 1.0747 | 1.091 | 1.0784 | 1.0915
Pressures | Keller | 13.75 |  | 12.8 |  | 12.85 |  | 12.9 | 12.9 |  |  | 12.95 | 12.98 |  | 12.99 | [5 empty] | 13.02 | 13 | 13.01 | 12.99 | 13.13 |  |  | 12.96 | 12.98 | 12.97 | 13.02 | 13.3 |  | 13.22 | 13.02 | 13.02 |  | 13.15 | 12.97 | 13.02 | 13.055 | 13.07 | 13.08 |  |  | 12.98 | 13.04 | 13 | 12.97 | 12.98 | 12.95 | 13.03 |  | 12.99 | 13.01 | 12.73 | 12.59 | 13 |  |  |  | 12.98 | 12.97 | 12.99 | 11.24 | 11.245 | 12.99 | 11 | 13.01 | 11.01 | 12.98
directly after capillaries | ABS press 00.01 | 1.7 |  | broken |  | broken | [5 empty] | 1.76 | 1.7 |  | 1.71 | [5 empty] | 1.7 | 1.75 | 1.81 | 1.68 | 1.63 |  |  | 1.64 | 1.65 | 1.69 | 1.73 | 1.73 |  | 1.63 | 1.62 | 1.72 |  | 1.72 | 1.68 | 1.69 | 1.74 | 1.74 | 1.73 |  |  | 1.64 | 1.67 | 1.71 | 1.75 | 1.59 | 1.74 | 1.67 |  | 1.67 | 1.74 | 1.7 | 1.7 | 1.67 |  |  |  | 1.68 | 1.73 | 1.73 | 1.66 | 1.64 | 1.69 | 1.68 | 1.7 | 1.68 | 1.63
differential across caps | DiffPCAP (00.06) | 12.14 |  | 13.43 | WRONG! | 13.33 | WRONG! |  |  |  |  | 11.17 | 11.18 |  | 11.19 |  |  | tomorrow - change DP over HEX vapour, run at higher TlbHEX, add extra temp sensors just after heater and TvbHEX |  |  | 11.28 | 11.2 | 11.2 | 11.29 | 11.46 |  |  | 11.28 | 11.27 | 11.24 | 11.25 | 11.54 |  | 11.53 | 11.37 | 11.26 |  | 11.41 | 11.25 | 11.28 | 11.31 | 11.32 | 11.33 |  |  | 11.2 | 11.23 | 11.15 | 11.1 | 11.25 | 11.08 | 11.24 |  | 11.11 | 11.06 | 10.81 | 10.69 | 11.1 |  |  |  | 11.25 | 11.18 | 11.21 | 9.53 | 9.54 | 11.26 | 9.27 | 11.27 | 9.29 | 11.3
DP calc | [27 empty] | 11.32 | 11.33 | 11.28 | 11.29 | 11.57 |  | 11.59 | 11.4 | 11.3 |  | 11.43 | 11.29 | 11.33 | 11.315 | 11.33 | 11.35 |  |  | 11.34 | 11.37 | 11.29 | 11.22 | 11.39 | 11.21 | 11.36 |  | 11.32 | 11.27 | 11.03 | 10.89 | 11.33 |  |  |  | 11.3 | 11.24 | 11.26 | 9.58 | 9.605 | 11.3 | 9.32 | 11.31 | 9.33 | 11.35
diff DP meas & calc | [27 empty] | 0.04 | 0.06 | 0.04 | 0.04 | 0.03 |  | 0.06 | 0.03 | 0.04 |  | 0.02 | 0.04 | 0.05 | 0.005 | 0.01 | 0.02 |  |  | 0.14 | 0.14 | 0.14 | 0.12 | 0.14 | 0.13 | 0.12 |  | 0.21 | 0.21 | 0.22 | 0.2 | 0.23 |  |  |  | 0.05 | 0.06 | 0.05 | 0.05 | 0.065 | 0.04 | 0.05 | 0.04 | 0.04 | 0.05
Cap temperatures | before cap (MoTe06 06:12) | -20.33 |  | ---- | NOT CONNECTED! | [6 empty] | -17.14 | -9.11 |  | -10.19 | [5 empty] | -7.09 | -17.32 | -19.28 | -21.16 | -5.25 |  |  | -4.32 | -8.65 | -15.93 | -16.07 | 2.62 |  | -7.85 | -19.67 | -18.84 |  | -5.31 | -18.77 | -13.85 | -10.55 | -9.06 | -8.07 |  |  | -5.05 | -11.69 | -10.06 | -4.72 | -5.76 | -4.37 | -14.3 |  | -3.79 | -4.52 | -4.28 | -4.38 | -14.48 |  |  |  | -3.52 | -3.68 | -7.17 | -5.31 | -3.45 | -12.84 | -10.02 | -14.87 | -14 | -15.61
| before cap (MoTe03 06.09) | -21.44 |  | -16.53 |  | -16.78 |  | -12.84 | -11.53 |  |  | -18.66 | -10.28 |  | -11.41 | [5 empty] | -6.14 | -15.9 | -17.82 | -19.64 | -4.47 |  |  | -6.63 | -11.37 | -19.08 | -19.22 | 0.96 |  | -8.22 | -20.15 | -19.33 |  | -6.27 | -20.13 | -15.1 | -11.79 | -10.34 | -9.34 |  |  | -5.85 | -12.67 | -10.99 | -5.56 | -6.65 | -5.26 | -15.47 |  | -3.92 | -4.65 | -4.44 | -4.54 | -14.51 |  |  |  | -3.71 | -3.52 | -6.91 | -5.15 | -3.35 | -12.11 | -9.28 | -13.55 | -12.71 | -14.14
| average TlbCap | [19 empty] | -6.615 | -16.61 | -18.55 | -20.4 | -4.86 |  |  | -5.475 | -10.01 | -17.505 | -17.645 | 1.79 |  | -8.035 | -19.91 | -19.085 |  | -5.79 | -19.45 | -14.475 | -11.17 | -9.7 | -8.705 |  |  | -5.45 | -12.18 | -10.525 | -5.14 | -6.205 | -4.815 | -14.885 |  | -3.855 | -4.585 | -4.36 | -4.46 | -14.495 |  |  |  | -3.615 | -3.6 | -7.04 | -5.23 | -3.4 | -12.475 | -9.65 | -14.21 | -13.355 | -14.875
| after cap (MoTe05 06.11) | -18.74 |  | -23.08 |  | -21.57 |  | -20.31 | -19.84 |  |  | -17.54 | -14.52 |  | -14.72 | [5 empty] | -15.6 | -19.61 | -20.23 | -21.91 | -15.5 |  |  | -17.2 | -18.8 | -21.95 | -21.83 | -16.51 |  | -18.35 | -22.57 | -21.57 |  | -16.11 | -22.21 | -19.3 | -17.82 | -17.24 | -16.93 |  |  | -17.21 | -21.33 | -20.43 | -17.01 | -19.16 | -16.44 | -22.12 |  | -15.86 | -16.44 | -16.41 | -16.67 | -22.24 |  |  |  | -3.14 | -3.35 | -7.37 | -5.15 | -3.43 | -14.08 | -10.57 | -15.71 | -14.59 | -16.35
| after cap (MoTe04 06.10) | -19.54 |  | -15.74 | WRONG! | -14.62 |  | -13.39 | -12.72 |  |  | -21.01 | -18.26 |  | -18.43 | [5 empty] | -16.69 | -20.28 | -20.87 | -22.56 | -16.8 |  |  | -16.06 | -17.8 | -21.17 | -21.07 | -14.97 |  | -17.16 | -21.77 | -20.8 |  | -14.97 | -21.43 | -18.42 | -16.85 | -16.25 | -15.89 |  |  | -18.12 | -21.96 | -21.13 | -17.77 | -20.03 | -17.44 | -22.74 |  | -16.74 | -17.25 | -17.25 | -17.6 | -22.8 |  |  |  | -3.58 | -3.81 | -7.89 | -5.61 | -2.96 | -13.59 | -10.1 | -15.31 | -14.19 | -15.89
| average TlaCap | -19.14 |  | -19.41 |  | -18.095 |  | -16.85 | -16.28 |  |  | -19.275 | -16.39 |  | -16.575 | [5 empty] | -16.145 | -19.945 | -20.55 | -22.235 | -16.15 |  |  | -16.63 | -18.3 | -21.56 | -21.45 | -15.74 |  | -17.755 | -22.17 | -21.185 |  | -15.54 | -21.82 | -18.86 | -17.335 | -16.745 | -16.41 |  |  | -17.665 | -21.645 | -20.78 | -17.39 | -19.595 | -16.94 | -22.43 |  | -3.855 | -16.845 | -16.83 | -17.135 | -22.52 | This is the correct TlaCAP (before TvaCAP) |  |  | -3.36 | -3.58 | -7.63 | -5.38 | -3.195 | -13.835 | -10.335 | -15.51 | -14.39 | -16.12
HEX efficiency/temps | TlbHEX (MoTe02 06.04) | 21 |  | 18.2 |  | 19.47 |  | 23.33 | 23.59 |  |  | 24.03 | 26 |  | 25.94 | 28 |  |  |  |  | 35 | 33.75 | 33.65 | 34.94 | 35 |  |  | 33.95 | 33.56 | 33.44 | 33.71 | 34.47 |  | 34.54 | 20.38 | 20.42 |  | 33.88 | 33.61 | 33.88 | 34.17 | 34.37 | 34.57 |  |  | 30.83 | 30.79 | 31.6 | 33.03 | 30.89 | 32.79 | 19.03 |  | 34.59 | 34.71 | 34.94 | 34.98 | 20.85 |  | using TlbFilter (MoTe01 06.01) |  | 34.63 | 34.79 | 29.85 | 30.12 | 29.97 | 24.8 | 24.72 | 20.54 | 20.3 | 20.07
| TlaHEX (CaTe03 06.06) | -22.21 |  | -20.13 |  | -20.34 |  | -15.1 | -11.51 |  |  | -17 | -8.32 |  | -9.64 | 7.7 |  |  |  |  | -4.56 | -14.33 | -16.25 | -18.04 | -2.78 |  |  | -3.51 | -7.8 | -14.95 | -15.13 | 2.62 |  | -7.66 | -21.2 | -20.35 |  | -5.99 | -21.12 | -15.42 | -11.88 | -10.08 | -9.08 |  |  | -6 | -13 | -11 | -5.6 | -7 | -5.3 | -16 |  | -6.6 | -7.58 | -7.29 | -7.45 | -20.21 |  |  |  | -7 | -7.44 | -11.93 | -9.54 | -7.09 | -18.93 | -15.15 | -20.69 | -19.8 | -21.64
| TvbHEX (PiTe23 06.05) | -26.19 |  | -26.12 |  | -25.03 |  | -24.71 | -24.66 |  |  | -23.72 | -23.82 |  | -23.88 | -12.7 |  |  |  |  | -22.93 | -22.98 | -22.87 | -24.96 | -25.12 |  |  | -23.98 | -23.94 | -24.12 | -23.95 | -23.15 |  | -24.22 | -25.52 | -24.27 |  | -22.98 | -24.7 | -24.57 | -24.58 | -24.63 | -24.63 |  |  | -23.87 | -24.05 | -23.77 | -23.52 | -24.44 | -23.63 | -24.38 | WRONG!! Should be -24C | -14.3 | -14.63 | -14.8 | -15.07 | -17.58 |  |  |  | -24.22 | -24.63 | -24.68 | -25.55 | -25.9 | -25.37 | -25.27 | -25.38 | -25.39 | -25.91
| TvaHEX (CaTe02 06.03) | -14.82 |  | -20.25 |  | -3.44 |  | 2.6 | 4.04 |  |  | -18.71 | 10 |  | 9.28 | [5 empty] | -24.02 | -23.61 | -23.5 | -16.4 | 15.35 |  |  | -24.93 | -24.98 | -24.84 | -24.46 | 16.91 |  | -25.1 | -25.32 | -23.95 |  | -24.07 | -25.37 | -8.5 | 4.69 | 10.2 | 12.16 |  |  | -25.1 | -25.15 | -25.05 | 5.75 | -25.82 | 7.67 | -24.8 |  | -24.55 | 5.31 | 8.34 | 8.96 | -24.15 |  |  |  | -24.59 | 8.63 | -9.57 | 9.38 | 10.83 | -25.81 | 0.24 | -26.07 | -18.15 | -25.19
| HEX efficiency | 0.91936 |  | 0.86719 |  | 0.87552 |  | 0.77904 | 0.7078 |  |  | 0.87242 | 0.6864 |  | 0.71245 | 0.39038 |  |  |  |  | 0.67051 | 0.83255 | 0.86557 | 0.89888 | 0.64034 |  |  | 0.64642 | 0.71855 | 0.84244 | 0.8463 | 0.54472 |  | 0.72087 | 0.93691 | 0.91783 |  | 0.68884 | 0.95001 | 0.85176 | 0.79165 | 0.76152 | 0.74526 | 0 | 0 | 0.65968 | 0.79923 | 0.76619 | 0.67736 | 0.69029 | 0.67072 | 0.81408 |  | 0.70302 | 0.72032 | 0.71649 | 0.7194 | 0.9155 |  |  |  | 0.71005 | 0.71832 | 0.77586 | 0.73282 | 0.68668 | 0.89611 | 0.81835 | 0.92568 | 1.0086 | 0.92545
| Temp after detectors (CaTe04 06.07) | [6 empty] | -21.7 | -21.73 |  |  | -22.11 | -21.06 |  | -21.05 | [5 empty] | -22 | -20.88 | -20.54 | -22.34 | -22.82 |  |  | -23.08 | -22.02 | -21.69 | -21.24 | -21.14 |  | -23.14 | -23.92 | -22.77 |  | -21.91 | -21.82 | -21.63 | -21.61 | -21.63 | -21.69 |  |  | -22.69 | -21.68 | -21.03 | -20.53 | -23.21 | -20.64 | -23.5 |  | -22.27 | -20.68 | -20.98 | -21.28 | -23.75 |  |  |  | -22.1 | -20.83 | -20.85 | -21.81 | -22.09 | -21.41 | -21.49 | -21.36 | -21.6 | -24.28
Other Pressures | DiffP caps (InPr21 00.06) | 0.067 |  | 13.35 | WRONG! | 13.33 | [5 empty] | 11.1 | 11.21 |  | 11.25 | [5 empty] | 11.29 | 11.21 | 11.2 | 11.3 | 11.48 |  |  | 11.27 | 11.27 | 11.24 | 11.25 | 11.53 |  | 11.55 | 11.36 | 11.28 |  | 11.4 | 11.25 | 11.27 | 11.31 | 11.32 | 11.33 |  |  | 11.2 | 11.22 | 11.16 | 11.1 | 11.26 | 11.08 | 11.23 |  | 11.11 | 11.06 | 10.81 | 10.68 | 11.11 |  |  |  | 11.24 | 11.18 | 11.2 | 9.52 | 9.55 | 11.25 | 9.27 | 11.28 | 9.29 | 11.29
| diffP across HEX liquid (BaPr16 00.13) | 0.74 |  | 2.67 | WRONG! | 2.69 | [5 empty] | 1 | 0.96 |  | 0.97 | [5 empty] | 0.94 | 1.03 | 1.05 | 1.06 | 0.93 |  |  | 1.08 | 1.12 | 1.21 | 1.22 | 1.01 |  | 1.11 | 1.23 | 1.22 |  | 1.09 | 1.22 | 1.17 | 1.14 | 1.13 | 1.12 |  |  | 1.17 | 1.24 | 1.22 | 1.19 | 1.18 | 1.18 | 1.26 |  | 1.17 | 1.18 | 0.15 | 1.14 | 1.26 |  |  |  | 1.16 | 1.17 | 1.21 | 1 | 0.99 | 1.24 | 1.01 | 1.26 | 1.04 | 1.27
| DiffP on-cylind (InPr03 00.04) | 0.124 |  | 0.27 | WRONG! | 0.32 | [5 empty] | 0.06 | 0.13 |  | 0.13 | [5 empty] | 0.08 | 0.08 | 0.09 | 0.11 | 0.13 |  |  | 0.08 | 0.08 | 0.09 | 0.11 | 0.13 |  | 0.08 | 0.08 | 0.07 |  | 0.08 | 0.11 | 0.13 | 0.13 | 0.13 | 0.13 |  |  | 0.07 | 0.08 | 0.12 | 0.14 | 0.07 | 0.14 | 0.06 |  | 0.05 | 0.12 | 0.12 | 0.12 | 0.05 |  |  |  | 0.07 | 0.14 | 0.13 | 0.13 | 0.13 | 0.13 | 0.12 | 0.13 | 0.11 | 0.07
| DiffP Hex vapour (BaPr15 00.03) | 0.132 |  | 2.08 | WRONG! | 2.08 | [5 empty] | 0.42 | 0.42 | WRONG!! | 0.42 | [5 empty] | 0.03 | 0.03 | 0.04 | 0.04 | 0.05 |  |  | 0.04 | 0.04 | 0.04 | 0.05 | 0.05 |  | 0.03 | 0.03 | 0.03 |  | 0.03 | 0.05 | 0.05 | 0.05 | 0.06 | 0.06 |  |  | 0.03 | 0.05 | 0.05 | 0.06 | 0.03 | 0.06 | 0.06 |  | 0.03 | 0.06 | 0.06 | 0.06 | 0.02 |  |  |  | 0.03 | 0.06 | 0.06 | 0.05 | 0.05 | 0.06 | 0.05 | 0.06 | 0.05 | 0.05
| Press BPR (BaPR01 00.02) | 0.057 |  | 1.33 |  | 1.32 |  | 1.32 | 1.32 |  |  | 1.54 | 1.38 |  | 1.37 | [5 empty] | 1.48 | 1.51 | 1.52 | 1.33 | 1.26 |  |  | 1.38 | 1.39 | 1.39 | 1.38 | 1.36 |  | 1.36 | 1.39 | 1.51 |  | 1.49 | 1.32 | 1.31 | 1.29 | 1.28 | 1.28 |  |  | 1.36 | 1.35 | 1.33 | 1.32 | 1.3 | 1.31 | 1.41 |  | 1.4 | 1.31 | 1.3 | 1.27 | 1.39 |  |  |  | 1.42 | 1.31 | 1.3 | 1.28 | 1.26 | 1.26 | 1.32 | 1.27 | 1.31 | 1.36
Detector heating | Volts | 160 |  | 0 |  | 153 |  | 153 | 153.5 |  |  | 0 | 152.7 |  | 152.8 | [5 empty] | 0 | 75 | 107.4 | 130 | 144 |  |  | 0 | 76.3 | 108.7 | 131.6 | 151.7 |  | 0 | 0 | 0 |  | 0 | 131.2 | 138.8 | 143.3 | 147.9 | 149.3 | 151.7 |  | 0 | 108.5 | 132.1 | 151.5 | 2 | 152.8 | 0 |  | 0 | 150.5 | 150.5 | 149.9 | 0 |  |  |  | 0 | 151.6 | 151.9 | 151.7 | 153.1 | 153.1 | 152.5 | 153.5 | 151.5 | 0
| Current | 2.17 |  | 0 |  | 2.3 |  | 2.3 | 2.3 |  |  | 0 | 2.31 |  | 2.31 | [5 empty] | 0 | 1.13 | 1.626 | 1.968 | 2.17 |  |  | 0 | 1.174 | 1.65 | 1.993 | 2.295 |  | 0 | 0 | 0 |  | 0 | 2.012 | 2.11 | 2.17 | 2.23 | 2.262 | 2.292 |  | 0 | 1.65 | 2.001 | 2.289 | 0.01 | 2.306 | 0 |  | 0 | 2.274 | 2.275 | 2.266 | 0 |  |  |  | 0 | 2.29 | 2.293 | 2.292 | 2.313 | 2.311 | 2.301 | 2.3 | 2.286 | 0
| Power on detector structure [W] | 347.2 |  | 0 |  | 351.9 |  | 351.9 | 353.05 |  |  | 0 | 352.737 |  | 352.968 | [5 empty] | 0 | 84.75 | 174.6324 | 255.84 | 312.48 |  |  | 0 | 89.5762 | 179.355 | 262.2788 | 348.1515 |  | 0 | 0 | 0 |  | 0 | 263.9744 | 292.868 | 310.961 | 329.817 | 337.7166 | 347.6964 | 0 | 0 | 179.025 | 264.3321 | 346.7835 | 0.02 | 352.3568 | 0 |  | 0 | 342.237 | 342.3875 | 339.6734 | 0 |  |  |  | 0 | 347.164 | 348.3067 | 347.6964 | 354.1203 | 353.8141 | 350.9025 | 353.05 | 346.329 | 0
| % | 1.002 |  | 0 |  | 1.0156 |  | 1.0156 | 1.0189 |  |  | 0 | 1.018 |  | 1.0187 | [5 empty] | 0 | 0.24459 | 0.50399 | 0.73835 | 0.90182 |  |  | 0 | 0.25852 | 0.51762 | 0.75694 | 1.0048 |  | 0 | 0 | 0 |  | 0 | 0.76183 | 0.84522 | 0.89743 | 0.95185 | 0.97465 | 1.0035 | 0 | 0 | 0.51667 | 0.76286 | 1.0008 | 5.772e-05 | 1.0169 | 0 |  | 0 | 0.9877 | 0.98813 | 0.9803 | 0 |  |  |  | 0 | 1.0019 | 1.0052 | 1.0035 | 1.022 | 1.0211 | 1.0127 | 1.0189 | 0.99951 | 0
| Power from I^2R (R=66.2) | 0.89965 |  | 0 |  | 1.0107 |  | 1.0107 | 1.0107 |  |  | 0 | 1.0195 |  | 1.0195 | [5 empty] | 0 | 0.24396 | 0.50512 | 0.73995 | 0.89965 |  |  | 0 | 0.26332 | 0.52014 | 0.75887 | 1.0063 |  | 0 | 0 | 0 |  | 0 | 0.77341 | 0.85059 | 0.89965 | 0.95009 | 0.97755 | 1.0037 | 0 | 0 | 0.52014 | 0.76498 | 1.001 | 1.9105e-05 | 1.016 | 0 |  | 0 | 0.98795 | 0.98882 | 0.98101 | 0 |  |  |  | 0 | 1.0019 | 1.0045 | 1.0037 | 1.0221 | 1.0204 | 1.0116 | 1.0107 | 0.99841 | 0
Vapor heater after HEX | Volts | pid |  | pid |  | pid |  | pid | pid |  |  | pid | pid |  | pid | [5 empty] | pid | pid | pid | pid | pid |  |  | pid | pid | pid | pid | pid |  | pid | pid | pid |  | pid | pid | pid | pid | pid | pid | pid | pid | pid | pid | pid | pid | pid | pid | pid |  | pid | pid | pid | pid | pid |  |  |  | pid | pid | pid | pid | pid | pid | pid | pid | pid | pid
| Current | [10 empty] | 54% | 8.3% |  | 8.7% | [5 empty] | 43.8% | 32.7% |  | 14% | 3% |  |  | 49% |  | 30% | 18.5% | 2.4% |  | 49% | 65% | 67% |  | 47.7% |  | 14% |  |  | 7% |  |  | 55% | 33% | 21% | 12% | 54% | 9% | 77% |  | 60% | 10% | 6% | 11% | 77% |  |  |  | 49% | 6% | 14% | 8% | 5.5% | 18.5% | 12% | 23% | 15.4% | 74.4%
Power P=VI
Power on heater | P=V2/R, R=14 - need tocheck
| Temp after vapor heater (PiT12 05.17) |  |  | 21.39 |  | 22.09 |  | 22.5 | 22.61 |  |  | 20.41 | 22.7 |  | 23.06 | [5 empty] | 20.68 | 21.41 | 21.74 | 22.53 | 21.75 |  |  | 20.43 | 21.15 | 21.82 | 22.06 | 21.61 |  | 20.41 | 21.64 | 21.47 |  | 20.5 | 22 | 22.51 | 22.52 | 22.53 | 21.86 |  |  | 22.84 | 21.74 | 22.08 | 22.75 | 22.99 | 23 | 22.1 |  | 22.35 | 22.7 | 22.8 | 22 | 21.72 |  |  |  | 20.18 | 22.91 | 22.4 | 22.7 | 22.51 | 21.95 | 22.93 | 21.87 | 22.34 | 21.37
VQ inlet |  | 7.551% |  | 7.189% |  | 7.472% |  | 8.483% | 9.047% |  |  | 4.822% | 8.056% |  | 7.918% | [5 empty] | 7.391% | 3.305% | 2.528% | 2.937% | 9.661% |  |  | 7.963% | 6.112% | 2.771% | 2.709% | 8.063% |  | 6.995% | 3.6% | 3.337% |  | 8.103% | 3.109% | 6.167% | 7.825% | 8.514% | 8.875% |  |  | 6.726% | 2.605% | 3.243% | 6.657% | 5.237% | 7.261% | 2.108% |  | 11.92% | -2.523% | -2.31% | -2.346% | -5.537% |  |  |  | 22.57% | 22.73% | 18.4% | 21.67% | 24.35% | 12.41% | 16.07% | 10.62% | 11.83% | 10.5%
VQ outlet |  | 63.54% |  | 7.189% |  | 63.53% |  | 64.91% | 65.77% |  |  | 4.822% | 72.66% |  | 72.55% | [5 empty] | 7.391% | 18.36% | 33.34% | 46.88% | 67.37% |  |  | 7.963% | 21.05% | 31.43% | 44.72% | 69.63% |  | 6.995% | 3.6% | 3.337% |  | 8.103% | 45.09% | 53.48% | 58.99% | 63.6% | 65.09% |  |  | 6.726% | 30.81% | 45.28% | 62.24% | 5.24% | 64.46% | 2.108% |  | 11.92% | 56.06% | 57.14% | 57.56% | -5.537% |  |  |  | 22.57% | 79.07% | 73.63% | 82.62% | 86.2% | 67.49% | 77% | 65.76% | 71.61% | 10.5%
Hliq_sat |  | 171.6408 |  | 171.7185 |  | 172.9292 |  | 173.2846 | 173.3401 |  |  | 174.3842 | 174.2731 |  | 174.2065 | [5 empty] | 175.2616 | 175.2061 | 175.3283 | 173.0069 | 172.8292 |  |  | 174.0954 | 174.1398 | 173.9399 | 174.1287 | 175.0173 |  | 173.8288 | 172.3849 | 173.7733 |  | 175.2061 | 173.2957 | 173.4401 | 173.429 | 173.3735 | 173.3735 |  |  | 174.2176 | 174.0177 | 174.3287 | 174.6063 | 173.5845 | 174.4842 | 173.6511 |  | 184.847 | 184.4805 | 184.2916 | 183.9918 | 181.2039 |  |  |  | 173.8288 | 173.3735 | 173.3179 | 172.3516 | 171.9629 | 172.5515 | 172.6626 | 172.5404 | 172.5293 | 171.9518
Hvap_sat |  | 275.3419 |  | 275.3823 |  | 276.0102 |  | 276.1946 | 276.2234 |  |  | 276.7649 | 276.7073 |  | 276.6727 | [5 empty] | 277.22 | 277.1912 | 277.2546 | 276.0505 | 275.9584 |  |  | 276.6151 | 276.6382 | 276.5345 | 276.6324 | 277.0933 |  | 276.4769 | 275.7279 | 276.4481 |  | 277.1912 | 276.2003 | 276.2752 | 276.2695 | 276.2407 | 276.2407 |  |  | 276.6785 | 276.5748 | 276.7361 | 276.8801 | 276.3501 | 276.8168 | 276.3847 |  | 282.1918 | 282.0017 | 281.9037 | 281.7482 | 280.3022 |  |  |  | 276.4769 | 276.2407 | 276.2119 | 275.7106 | 275.509 | 275.8143 | 275.872 | 275.8086 | 275.8028 | 275.5032
Hdiff_sat |  | 103.7012 |  | 103.6638 |  | 103.081 |  | 102.91 | 102.8832 |  |  | 102.3807 | 102.4342 |  | 102.4662 | [5 empty] | 101.9584 | 101.9851 | 101.9263 | 103.0436 | 103.1292 |  |  | 102.5197 | 102.4983 | 102.5946 | 102.5037 | 102.076 |  | 102.648 | 103.343 | 102.6747 |  | 101.9851 | 102.9046 | 102.8351 | 102.8405 | 102.8672 | 102.8672 |  |  | 102.4609 | 102.5571 | 102.4074 | 102.2738 | 102.7656 | 102.3326 | 102.7335 |  | 97.3448 | 97.5212 | 97.6121 | 97.7564 | 99.0983 |  |  |  | 102.648 | 102.8672 | 102.8939 | 103.359 | 103.5461 | 103.2628 | 103.2093 | 103.2681 | 103.2735 | 103.5515
Hliq_end_cap |  | 179.4712 |  | 179.1713 |  | 180.6319 |  | 182.0147 | 182.6478 |  |  | 179.3213 | 182.5256 |  | 182.3201 | [5 empty] | 182.7977 | 178.5771 | 177.9051 | 176.0336 | 182.7922 |  |  | 182.2591 | 180.4042 | 176.7833 | 176.9055 | 183.2476 |  | 181.0095 | 176.1058 | 177.1998 |  | 183.4697 | 176.4945 | 179.7822 | 181.476 | 182.1313 | 182.5034 |  |  | 181.1095 | 176.6889 | 177.6497 | 181.4149 | 178.9658 | 181.9147 | 175.817 |  | 196.4483 | 182.0203 | 182.0369 | 181.6982 | 175.717 |  |  |  | 196.998 | 196.7537 | 192.2554 | 194.7544 | 197.1813 | 185.3635 | 189.2509 | 183.503 | 184.747 | 182.8255
Liquid heater before HEX | Volts (approximate, manual) | 60 |  | 110 |  | 150 |  | 150 | 150 |  |  | 155 | 155 |  | 155 | [5 empty] | 210 | 215 | 215 | 215 | 215 |  |  | 220 | 220 | 220 | 220 | 215 |  | 215 | 100 | 100 |  | 215 | 215 | 215 | 215 | 215 | 215 |  |  | 215 | 215 | 215 | 215 | 215 | 215 | 100 |  | 220 | 220 | 220 | 220 | 0 |  |  |  | 220 | 220 | 190 | 185 | 185 | 145 | 142 | 85 | 85 | 85
| temperature before filter (06.00) | 22.64 |  | 19.47 |  | 21.35 |  | 24.01 | 24.21 |  |  | 25.36 | 26.6 |  | 26.55 | [5 empty] | 35 | 35 | 35 | 35 | 35.7 |  |  | 35.22 | 34.82 | 34.72 | 34.75 | 35.15 |  | 34.54 | 21.74 | 21.74 |  | 35.3 | 34.62 | 34.82 | 34.98 | 35.12 | 35.27 |  |  | 33.54 | 33.55 | 33.73 | 33.81 | 33.8 | 33.94 | 22 |  | 34.54 | 34.64 | 34.88 | 34.89 | 21.48 |  |  |  | 34.4 | 34.68 | 29.93 | 30.21 | 30.05 | 25.14 | 25.04 | 21.01 | 20.89 | 20.63
| Tljustbefore HEX (MoTe02 06.04) | [60 empty] | 31.09 | 33.09 | 28.01 | 28.81 | 28.78 | 22.89 | 23.43 | 18.21 | 18.86 | 17.77
comments |  |  |  | 16:21 power onto detector heater | [5 empty] | 16:44 turn system off |  | 15:38 turn detector power to 100% |  | 16:40 bypass massflow meter | system started to heat up - Tvafter Det too hot! Tuned the power down to 40% (100V) then back to 100%. | 17:16 inlet heater upto 170V |  |  |  |  | At 5.77 g/s with -7C before capillary, according to Danfoss! What is max power we can apply! 10:33 applay some power | 10:52 increase power to 50% | 11:12 power to 75% | 11:36 power to 90% | not really stable - temps increasing. | 11:50 - turn power off and close down the system | NOTE - on turning powerr off - system as was before turning power on | 11:51 power to 25% | 12:11 power to 50% | 13:41 power to 75% | 14:05 to 100% power | system is very much on the edge of stability! cant increase the pressure any more - at max! system is unstable - warming up! |  | down to 0% power then to TlbHEX =20C without touching anything! | 14:53 TlHEX to 20C | 15:24 change BPR to give 1.75Pevap | need more massflow in the system. | 18:11 up to 75% power | 18:30 up to 85% | 18:53 to 90% | 19:24 upto 95% power | 19:45 up to 97% | 20:09 up to 100% for 5 minutes | system off at 20:115 |  | 14:16 up to 50% power | 14:32 to 75% power | 14:53 to 100% | 15:16 0%, 35C | 15:30 to 100%, 35C | 15:50 to 0%, 20C, adjust to get correct BPR | 16:20 system off |  | 19:00 det power to 100% | reduce inlet pressure | [6 empty] | 14:00 power to 100% - needed to reduce BPR slightly - measured 1.8 evap pressure at ABS 01 | 14:30 - reduce liquid heater power to get TlbHEX=30C | 15:03 reduce pressure to get TvaHEX=9C |  | 16:09 pressure up to 13bar and TlbHEX down to 25C | 16:39 reduce pressure to 11bar (kind of minimum) | 17:14 reduce TlbHEX to 20C Pressure =13bar | 17:41 drop input pressure to min at 11bar | 17:55 power off and back to 13bar | close system up for the night
[12 empty] | had to turn power down to 40% (100V) as system ran away. I changed the BPR which decreased the BP but increased the temperatures. Then a funny which caused run-away. The system ran okay after a reduction in power and then back to 100% power | [48 empty] | TlbHEX 35C, 100% power, p=13bar, what is massflow
[54 empty] | the temp at the end of the capillary is actually WRONG! It is measured on the copper pipe. Should re-run for a day to check the temperature. Should be only a deg higher/lower the TlbCAP, but need to check, could be lower if significant expansion in the capillary | [6 empty] | TlbHEX 30C, 100% power, p=13bar, what is massflow
TlbHEX 30C, 100% power, p=to min for stability, what is massflow
TlbHEX 25C, 100% power, p=13bar, what is massflow
TlbHEX 25C, 100% power, p=to min for stability, what is massflow
TlbHEX 20C, 100% power, p=13bar, what is massflow
[54 empty] | Worried about the TvbHEX - it seems too high. This was attached with copper tape for speed! | [6 empty] | TlbHEX 20C, 100% power, p=to min for stability, what is massflow
shut off one 0.68 capillary
TlbHEX 35C, 100% power, p=13bar, Is it stable, what is massflow
TlbHEX 35C, 100% power, increase P to stability (hopefully below 14bar!), what is massflow
p min set to 11bar. If system can take lower p then lower p not tried!

## Sheet2
Date / Time | date/time | 19:20 | 15:48 | 14:50 | 438:14 | 15:48 | 20:05
mass flow | by Danfoss | 6.58 | 6.55 | 6.68 | 6.6 | 6.55 | 6.36
| Temp in flowmeter | 16.24 | 16.48 | 16.52 | 16.43 | 16.48 | 16.32
| by Volume / time | 5.99 | 6.02 | 6.14 | 6.11 | 6.02 | 5.84
|  | +45deg, now with the keller and Huba P1 at capillary input level | incorrect level | +45deg | -45deg | +45deg, vapour end down | -45deg, vapour end up
Characteristic values: | Power on staves | 98.77% | 101.7% | 76.29% | 76.18% | 101.7% | 97.47%
| Inlet temp into HEX | 34.71 | 32.79 | 31.6 | 33.61 | 32.79 | 34.57
| Massflow | 5.99 | 6.02 | 6.14 | 6.11 | 6.02 | 5.84
|  | D/V=1.098 | Dan/Vol = 1.088 | Dan/Vol = 1.088 | Dan/Vol = 1.08 | Dan/Vol = 1.088 | Dan/Vol = 1.089
Pressures | Keller | 13.01 | 12.95 | 13 | 12.97 | 12.95 | 13.08
directly after capillaries | ABS press 00.01 | 1.74 | 1.74 | 1.71 | 1.68 | 1.74 | 1.73
differential across caps | DiffPCAP (00.06) | 11.06 | 11.08 | 11.15 | 11.25 | 11.08 | 11.33
Cap temperatures | before cap (MoTe06 06:12) | -4.52 | -4.37 | -10.06 | -18.77 | -4.37 | -8.07
| before cap (MoTe03 06.09) | -4.65 | -5.26 | -10.99 | -20.13 | -5.26 | -9.34
| Average TlbCap | -4.585 | -4.815
| after cap (MoTe05 06.11) | -16.44 | -16.44 | -20.43 | -22.21 | -16.44 | -16.93
| after cap (MoTe04 06.10) | -17.25 | -17.44 | -21.13 | -21.43 | -17.44 | -15.89
| Average TlaCap | -16.845 | -16.94 | -20.78 | -21.82 | -16.94 | -16.41
HEX efficiency/temps | TlbHEX (MoTe02 06.04) | 34.71 | 32.79 | 31.6 | 33.61 | 32.79 | 34.57
| TlaHEX (CaTe03 06.06) | -7.58 | -5.3 | -11 | -21.12 | -5.3 | -9.08
| TvbHEX (PiTe23 06.05) | -14.63 | -23.63 | -23.77 | -24.7 | -23.63 | -24.63
| TvaHEX (CaTe02 06.03) | 5.31 | 7.67 | -25.05 | -25.37 | 7.67 | 12.16
| HEX efficiency | 0.72032 | 0.67072 | 0.76619 | 0.95001 | 0.67072 | 0.74526
| Temp after detectors (CaTe04 06.07) | -20.68 | -20.64 | -21.03 | -21.82 | -20.64 | -21.69
Other Pressures | DiffP caps (InPr21 00.06) | 11.06 | 11.08 | 11.16 | 11.25 | 11.08 | 11.33
| diffP across HEX liquid (BaPr16 00.13) | 1.18 | 1.18 | 1.22 | 1.22 | 1.18 | 1.12
| DiffP on-cylind (InPr03 00.04) | 0.12 | 0.14 | 0.12 | 0.11 | 0.14 | 0.13
| DiffP Hex vapour (BaPr15 00.03) | 0.06 | 0.06 | 0.05 | 0.05 | 0.06 | 0.06
| Press BPR (BaPR01 00.02) | 1.31 | 1.31 | 1.33 | 1.32 | 1.31 | 1.28
Detector heating | Volts | 150.5 | 152.8 | 132.1 | 131.2 | 152.8 | 149.3
| Current | 2.274 | 2.306 | 2.001 | 2.012 | 2.306 | 2.262
| Power on detector structure [W] | 342.237 | 352.3568 | 264.3321 | 263.9744 | 352.3568 | 337.7166
| % | 0.9877 | 1.0169 | 0.76286 | 0.76183 | 1.0169 | 0.97465
| Power from I^2R (R=66.2) | 0.98795 | 1.016 | 0.76498 | 0.77341 | 1.016 | 0.97755
Vapor heater after HEX | Volts | pid | pid | pid | pid | pid | pid
| Current | 10% | 9% | 21% |  | 9% | 7%
Power P=VI
Power on heater | P=V2/R, R=14 - need tocheck
| Temp after vapor heater (PiT12 05.17) | 22.7 | 23 | 22.08 | 22 | 23 | 21.86
VQ inlet |  | -2.523% | 7.261% | 3.243% | 3.109% | 7.261% | 8.875%
VQ outlet |  | 56.06% | 64.46% | 45.28% | 45.09% | 64.46% | 65.09%
Hliq_sat |  | 184.4805 | 174.4842 | 174.3287 | 173.2957 | 174.4842 | 173.3735
Hvap_sat |  | 282.0017 | 276.8168 | 276.7361 | 276.2003 | 276.8168 | 276.2407
Hdiff_sat |  | 97.5212 | 102.3326 | 102.4074 | 102.9046 | 102.3326 | 102.8672
Hliq_end_cap |  | 182.0203 | 181.9147 | 177.6497 | 176.4945 | 181.9147 | 182.5034
Liquid heater before HEX | Volts (approximate, manual) | 220 | 215 | 215 | 215 | 215 | 215
| temperature before filter (06.00) | 34.64 | 33.94 | 33.73 | 34.62 | 33.94 | 35.27
comments |  | reduce inlet pressure | 15:50 to 0%, 20C, adjust to get correct BPR | 14:53 to 100% | 18:30 up to 85% | 15:50 to 0%, 20C, adjust to get correct BPR | 20:09 up to 100% for 5 minutes
Note on C21: this is too high due to bad thermal contact between the sensor and the pipe

## Sheet3
date/time | -45deg | 13:48 | 14:17-14:27 | 14:50-15:00 | 15:38-15:48 | 16:01-16:11 | 16:28-16:38 | 17:05-17:14 | 17:33-17:41 | 17:48-17:54 | 18:01-18:08 |  | +45deg | 20:05
by Danfoss |  | 6.48 | 6.527 | 6.649 | 6 | 5.935 | 6.745 | 5.997 | 6.764 | 6.05 | 6.8 |  |  | 6.36
by Volume / time |  | 5.99 | 5.99 | 6.13 | 5.52 | 5.53 | 6.22 | 5.58 | 6.2 | 5.61 | 6.23 |  |  | 5.84
% Mdot higher than 5.7g/s |  | 5.088% | 5.088% | 7.544% | -3.158% | -2.982% | 9.123% | -2.105% | 8.772% | -1.579% | 9.298% |  |  | 2.456%
Power on staves |  | 0% | 100.2% | 100.5% | 100.3% | 102.2% | 102.1% | 101.3% | 101.9% | 99.95% | 0% |  |  | 0%
Inlet temp into HEX |  | 34.63 | 34.79 | 29.85 | 30.12 | 29.97 | 24.8 | 24.72 | 20.54 | 20.3 | 20.07 |  |  | 34.57
Massflow |  | 5.99 | 5.99 | 6.13 | 5.52 | 5.53 | 6.22 | 5.58 | 6.2 | 5.61 | 6.23 |  |  | 5.84
% Danfoss high |  | 8.18% | 8.965% | 8.467% | 8.696% | 7.324% | 8.441% | 7.473% | 9.097% | 7.843% | 9.149% |  |  | 8.904%
Keller |  | 12.98 | 12.97 | 12.99 | 11.24 | 11.245 | 12.99 | 11 | 13.01 | 11.01 | 12.98 |  |  | 13.08
ABS press 00.01 |  | 1.68 | 1.73 | 1.73 | 1.66 | 1.64 | 1.69 | 1.68 | 1.7 | 1.68 | 1.63 | 1.7125 |  | 1.73
DiffPCAP (00.06) |  | 11.25 | 11.18 | 11.21 | 9.53 | 9.54 | 11.26 | 9.27 | 11.27 | 9.29 | 11.3 |  |  | 11.33
before cap (MoTe06 06:12) |  | -3.52 | -3.68 | -7.17 | -5.31 | -3.45 | -12.84 | -10.02 | -14.87 | -14 | -15.61 |  |  | -8.07
before cap (MoTe03 06.09) |  | -3.71 | -3.52 | -6.91 | -5.15 | -3.35 | -12.11 | -9.28 | -13.55 | -12.71 | -14.14 |  |  | -9.34
average TlbCap |  | -3.615 | -3.6 | -7.04 | -5.23 | -3.4 | -12.475 | -9.65 | -14.21 | -13.355 | -14.875 |  |  | -8.705
after cap (MoTe05 06.11) |  | -3.14 | -3.35 | -7.37 | -5.15 | -3.43 | -14.08 | -10.57 | -15.71 | -14.59 | -16.35 |  |  | -8
after cap (MoTe04 06.10) |  | -3.58 | -3.81 | -7.89 | -5.61 | -2.96 | -13.59 | -10.1 | -15.31 | -14.19 | -15.89 |  |  | -9
average TlaCap |  | -3.36 | -3.58 | -7.63 | -5.38 | -3.195 | -13.835 | -10.335 | -15.51 | -14.39 | -16.12 |  |  | -8.5
TlbHEX (MoTe02 06.04) |  | 34.63 | 34.79 | 29.85 | 30.12 | 29.97 | 24.8 | 24.72 | 20.54 | 20.3 | 20.07 |  |  | 34.57
TlaHEX (CaTe03 06.06) |  | -7 | -7.44 | -11.93 | -9.54 | -7.09 | -18.93 | -15.15 | -20.69 | -19.8 | -21.64 |  |  | -9.08
TvbHEX (PiTe23 06.05) |  | -24.22 | -24.63 | -24.68 | -25.55 | -25.9 | -25.37 | -25.27 | -25.38 | -25.39 | -25.91 |  |  | -24.63
TvaHEX (CaTe02 06.03) |  | -24.59 | 8.63 | -9.57 | 9.38 | 10.83 | -25.81 | 0.24 | -26.07 | -18.15 | -25.19 |  |  | 12.16
HEX efficiency |  | 0.71005 | 0.71832 | 0.77586 | 0.73282 | 0.68668 | 0.89611 | 0.81835 | 0.92568 | 1.0086 | 0.92545 |  |  | 0.74526
Temp after detectors (CaTe04 06.07) |  | -22.1 | -20.83 | -20.85 | -21.81 | -22.09 | -21.41 | -21.49 | -21.36 | -21.6 | -24.28 |  |  | -21.69
VQ inlet |  | 22.57% | 22.73% | 18.4% | 21.67% | 24.35% | 12.41% | 16.07% | 10.62% | 11.83% | 10.5% |  |  | 17.42%
VQ outlet |  | 22.57% | 79.07% | 73.63% | 82.62% | 86.2% | 67.49% | 77% | 65.76% | 71.61% | 10.5% |  |  | 73.63%