## Sheet1
Date |  | 26/01/2005 | [11 empty] | 15/02/2005 | [6 empty] | 16_02_2005 | [9 empty] | 17_02_2005 | [19 empty] | 26/02/2005 | [5 empty] | 28/02/2005 | [5 empty] | 2005-01-03 | [5 empty] | 2005-02-03 | [12 empty] | 2005-03-03
Time |  | 14:32 | 14:42 | 15:08 | 15:20 | 15:36 | 16:33 | 17:09 | 17:24 | 17:45 | 18:00 | 18:10 |  | 17:55 | 18:16 | 18:34 | 18:56 | 19:22 | 20:19 |  | 14:18 | 14:27 | 14:36 | 14:56 | 15:11 | 16:17 | 16:48 | 17:05 | 17:18 | 17:47 | 10:20 | 10:29 | 10:40 | 14:00 | 14:14 | 14:23 | 14:34 | 14:56 | 15:03 | 15:11 | 15:35 | 15:54 | 17:12 | 17:22 | 17:31 | 17:44 | 18:06 | 18:21 | 18:28 | 18:37 |  | 14:20 | 14:29 | 14:40 | 15:08 | 15:27 |  | 14:33 | 14:40 | 15:14 | 15:23 | 15:43 |  | 11:12 | 11:35 | 12:04 | 12:16 |  |  | 10:18 | 10:25 |  | 10:48 | 11:11 | 11:27 | 11:38 | 17:06 |  | 17:34 | 17:35 | 17:38 |  | 16:35 | 17:00 | 17:44
Capillary ID |  | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 |  | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 |  | 0.76 | 0.76 | 0.76 | 0.76 | 0.68 |  | 0.68 | 0.68 | 0.76 | 0.76 | 0.76 |  | 0.76 | 0.76 | 0.68 | 0.68 | 0.76 |  | 0.76 | 0.76 | 0.76 | 0.76 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 |  | 0.68 | 0.68 | 0.68
Capillary length |  | 3.44 | 3.44 | 3.44 | 3.44 | 3.44 | 3.44 | 3.446 | 3.446 | 3.446 | 3.446 | 3.446 | 2.63 | 3.446 | 3.446 | 3.446 | 3.446 | 3.446 | 2.63 |  | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.444 | 3.444 | 3.444 | 3.444 | 3.444 | 3.444 | 3.444 | 3.444 | 3.444 | 3.444 | 3.4 | 3.4 | 3.4 | 3.4 |  | 3.44 | 3.446 | 3.446 | 3.446 | 3.4 |  | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 |  | 2.75 | 2.75 | 3.1 | 3.1 | 2.9 |  | 2.72 | 2.72 | 2.65 | 2.65 | 3.1 | 3.2 | 3.2 | 3 | 3.05 | 3.12 | 3.05 | 3 |  | 2.97 | 2.92 | 3.1
Massflow |  | 2.05 | 2.003 | 2.003 | 1.94 | 1.872 | 2.037 | 1.965 | 1.956 | 1.88 | 1.821 | 1.972 | 2.32 | 1.776 | 1.829 | 1.883 | 1.968 | 1.918 | 2.226 |  | 2.265 | 2.349 | 2.273 | 2.176 | 2.228 | 2.1 | 2.03 | 2.14 | 2.21 | 2.29 | 1.552 | 1.523 | 1.477 | 1.455 | 1.423 | 1.384 | 1.474 | 1.521 | 1.569 | 1.609 | 1.659 | 1.58 | 1.54 | 1.497 | 1.451 | 1.425 | 1.313 | 1.345 | 1.395 | 1.452 |  | 2.157 | 2.017 | 2.02 | 2.104 | 1.53 |  | 1.634 | 1.705 | 2.15 | 2.082 | 2.1 |  | 2.275 | 2.24 | 1.6 | 1.77 | 0 |  | 2.29 | 2.292 | 2.29 | 2.293 | 1.6 | 1.56 | 1.64 | 1.633 | 1.58 | 1.715 | 1.59 | 1.62 |  | 1.615 | 1.655 | 1.735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Delta Pressure |  | 10.186 | 9.848 | 9.771 | 9.298 | 8.725 | 10.104 | 9.979 | 9.839 | 9.283 | 8.784 | 10.017 |  | 8.34 | 8.716 | 9.175 | 9.921 | 9.474 | 9.316 |  | 9.518 | 10.039 | 9.529 | 8.88 | 9.233 | 9.217 | 8.779 | 9.553 | 9.895 | 10.401 | 10.584 | 10.238 | 9.848 | 9.643 | 9.327 | 8.886 | 8.894 | 9.312 | 9.818 | 10.301 | 10.741 | 10.659 | 10.253 | 9.937 | 9.405 | 9.129 | 9.231 | 9.514 | 10.016 | 10.588 |  | 11.29 | 11.31 | 11.28 | 11.32 | 11.4 |  | 11.32 | 11.26 | 11.26 | 11.28 | 11.27 |  | 11.23 | 11.24 | 11.3 | 11.24 | 0 |  | 11.35 | 11.27 | 11.25 | 11.24 | 11.16 | 11.27 | 11.26 | 11.34 | 0 | 11.28 | 11.29 | 11.31 |  | 11.31 | 11.29 | 11.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tempreature |  | -14.94 | -15.39 | -14.9 | -14.905 | -15.215 | -15.265 | -15.18 | -15.48 | -14.98 | -14.985 | -14.465 |  | -14.545 | -15.16 | -14.975 | -15.005 | -15.15 | -12.755 |  | -14.38 | -15.01 | -14.87 | -15.02 | -14.885 | -7.033 | -6.9635 | -6.897 | -6.8825 | -7.314 | -15.14 | -15.18 | -15.2 | -14.77 | -15.01 | -14.885 | -14.945 | -15.07 | -15.18 | -14.845 | -14.96 | -7.5695 | -6.933 | -6.9605 | -7.369 | -7.247 | -7.019 | -7.422 | -7.614 | -7.058 |  | -7.055 | -7.055 | -7.085 | -14.49 | -7.5 |  | -7.26 | -6.885 | -6.98 | -7.275 | -6.875 |  | -7 | -7.18 | -6.92 | -7.165 | 0 |  | -6.94 | -7.305 | -6.95 | -7.095 | -6.855 | -6.945 | -7.04 | -7.03 | 0 | -6.92 | -7 | -7.5 |  | -6.735 | -7.89 | -6.735 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Sample |  | N1, 0.76 | N1, 0.76 | N1, 0.76 | N1, 0.76 | N1, 0.76 | N1, 0.76 | N8, 0.76 | N8, 0.76 | N8, 0.76 | N8, 0.76 | N8, 0.76 | N10, 0.76 | N6, 0.76 | N6, 0.76 | N6, 0.76 | N6, 0.76 | N6, 0.76 | N10, 0.76 |  | N10, 0.76 | N10, 0.76 | N10, 0.76 | N10, 0.76 | N10, 0.76 | N10, 0.76 | N10, 0.76 | N10, 0.76 | N10, 0.76 | N10, 0.76 | N2, 0.68 | N2, 0.68 | N2, 0.68 | N2, 0.68 | N2, 0.68 | N2, 0.68 | N7, 0.68 | N7, 0.68 | N7, 0.68 | N7, 0.68 | N7, 0.68 | N7, 0.68 | N7, 0.68 | N7, 0.68 | N7, 0.68 | N7, 0.68 | N2, 0.68 | N2, 0.68 | N2, 0.68 | N2, 0.68 |  | N1, 0.76 | N6, 0.76 | N8, 0.76 | N8, 0.76 | N2, 0.68 |  | N2, 0.68 | N7, 0.68 | N1, 0.76 | N6, 0.76 | N8, 0.76 |  | N8, 0.76 | N6, 0.76 | N2, 0.68 | N7, 0.68 | N1, 0.76 |  | N8, 0.76 | N8, 0.76 | N6, 0.76 | N6, 0.76 | N2, 0.68 | N10, 0.68 | N8, 0.68 | N2, 0.68 | N10, 0.68 | N8, 0.68 | N10, 0.68 | N2, 0.68 |  | N10, 0.68 | N2, 0.68 | N8, 0.65
Pressures
| Pressure before capillary (keller) | 11.9 | 11.5 | 11.51 | 11.02 | 10.45 | 11.8 | 11.7 | 11.53 | 11 | 10.49 | 11.7 |  | 10.05 | 10.46 | 10.9 | 11.65 | 11.2 | 11.05 |  | 11.22 | 11.75 | 11.22 | 10.57 | 10.93 | 10.93 | 10.47 | 11.25 | 11.6 | 12.1 | 12.3 | 11.94 | 11.54 | 11.37 | 11.02 | 10.62 | 10.6 | 11.04 | 11.52 | 12.01 | 12.42 | 12.37 | 11.99 | 11.64 | 11.1 | 10.87 | 10.92 | 11.22 | 11.72 | 12.29 |  | 12.96 | 12.98 | 12.96 | 12.97 | 13.02 |  | 13 | 12.97 | 12.97 | 12.98 | 12.98 |  | 12.98 | 12.99 | 13 | 12.96 |  |  | 12.99 | 13.02 | 13 | 13 | 12.9 | 13 | 13 | 13 |  | 12.99 | 13 | 13.02 |  | 13.02 | 13 | 12.95
| Pressure after capillary | 1.714 | 1.652 | 1.739 | 1.722 | 1.725 | 1.696 | 1.721 | 1.691 | 1.717 | 1.706 | 1.683 |  | 1.71 | 1.744 | 1.725 | 1.729 | 1.726 | 1.734 |  | 1.702 | 1.711 | 1.691 | 1.69 | 1.697 | 1.713 | 1.691 | 1.697 | 1.705 | 1.699 | 1.716 | 1.702 | 1.692 | 1.727 | 1.693 | 1.734 | 1.706 | 1.728 | 1.702 | 1.709 | 1.679 | 1.711 | 1.737 | 1.703 | 1.695 | 1.741 | 1.689 | 1.706 | 1.704 | 1.702 |  | 1.67 | 1.67 | 1.68 | 1.65 | 1.62 |  | 1.68 | 1.71 | 1.71 | 1.7 | 1.71 |  | 1.75 | 1.75 | 1.7 | 1.72 |  |  | 1.64 | 1.75 | 1.75 | 1.76 | 1.74 | 1.73 | 1.74 | 1.66 |  | 1.71 | 1.71 | 1.71 |  | 1.71 | 1.71 | 1.72
| DP over capillary | 10.256 | 9.957 | 9.836 | 9.425 | 8.823 | 10.16 | 10.068 | 9.959 | 9.403 | 8.9 | 10.133 | 9.5 | 8.453 | 8.829 | 9.237 | 10.056 | 9.594 | 9.432 |  | 9.616 | 10.157 | 9.659 | 8.984 | 9.323 | 9.304 | 8.907 | 9.658 | 9.999 | 10.554 | 10.7 | 10.37 | 9.987 | 9.802 | 9.471 | 9.025 | 9.015 | 9.441 | 9.957 | 10.413 | 10.884 | 10.818 | 10.411 | 10.091 | 9.534 | 9.268 | 9.358 | 9.656 | 10.155 | 10.7 |  | 11.4 | 11.45 | 11.44 | 11.44 | 11.54 |  | 11.47 | 11.38 | 11.39 | 11.41 | 11.42 |  | 11.38 | 11.38 | 11.42 | 11.41 |  |  | 11.47 | 11.42 | 11.41 | 11.37 | 11.4 | 11.42 | 11.41 | 11.49 |  | 11.42 |  |  |  | 11.49 | 11.44 | 11.41
| calculated DP | 10.186 | 9.848 | 9.771 | 9.298 | 8.725 | 10.104 | 9.979 | 9.839 | 9.283 | 8.784 | 10.017 |  | 8.34 | 8.716 | 9.175 | 9.921 | 9.474 | 9.316 |  | 9.518 | 10.039 | 9.529 | 8.88 | 9.233 | 9.217 | 8.779 | 9.553 | 9.895 | 10.401 | 10.584 | 10.238 | 9.848 | 9.643 | 9.327 | 8.886 | 8.894 | 9.312 | 9.818 | 10.301 | 10.741 | 10.659 | 10.253 | 9.937 | 9.405 | 9.129 | 9.231 | 9.514 | 10.016 | 10.588 |  | 11.29 | 11.31 | 11.28 | 11.32 | 11.4 |  | 11.32 | 11.26 | 11.26 | 11.28 | 11.27 |  | 11.23 | 11.24 | 11.3 | 11.24 |  |  | 11.35 | 11.27 | 11.25 | 11.24 | 11.16 | 11.27 | 11.26 | 11.34 |  | 11.28 | 11.29 | 11.31 |  | 11.31 | 11.29 | 11.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| diff between DPmeas & DPcalc | 0.07 | 0.109 | 0.065 | 0.127 | 0.098 | 0.056 | 0.089 | 0.12 | 0.12 | 0.116 | 0.116 |  | 0.113 | 0.113 | 0.062 | 0.135 | 0.12 | 0.116 |  | 0.098 | 0.118 | 0.13 | 0.104 | 0.09 | 0.087 | 0.128 | 0.105 | 0.104 | 0.153 | 0.116 | 0.132 | 0.139 | 0.159 | 0.144 | 0.139 | 0.121 | 0.129 | 0.139 | 0.112 | 0.143 | 0.159 | 0.158 | 0.154 | 0.129 | 0.139 | 0.127 | 0.142 | 0.139 | 0.112 |  | 0.11 | 0.14 | 0.16 | 0.12 | 0.14 |  | 0.15 | 0.12 | 0.13 | 0.13 | 0.15 |  | 0.15 | 0.14 | 0.12 | 0.17 |  |  | 0.12 | 0.15 | 0.16 | 0.13 | 0.24 | 0.15 | 0.15 | 0.15 |  | 0.14 |  |  |  | 0.18 | 0.15 | 0.18 | average | 0.1291 | std | 0.017321
| BPR | 1.6 | 1.55 | 1.62 | 1.6 | 1.6 | 1.59 | 1.61 | 1.59 | 1.6 | 1.58 | 1.58 |  | 1.675 | 1.701 | 1.686 | 1.69 | 1.683 | 1.692 |  | 1.664 | 1.664 | 1.653 | 1.65 | 1.646 | 1.675 | 1.654 | 1.646 | 1.638 | 1.648 | 1.686 | 1.667 | 1.657 | 1.686 | 1.646 | 1.694 | 1.673 | 1.691 | 1.665 | 1.663 | 1.643 | 1.67 | 1.687 | 1.663 | 1.652 | 1.702 | 1.656 | 1.673 | 1.658 | 1.638 |  | 1.62 | 1.62 | 1.63 | 1.62 | 1.59 |  | 1.65 | 1.67 | 1.65 | 1.66 | 1.67 |  | 1.71 | 1.7 | 1.66 | 1.68 |  |  | 1.59 | 1.71 | 1.72 | 1.72 | 1.69 | 1.7 | 1.7 | 1.62 |  | 1.68 |  |  |  | 1.67 | 1.67 | 1.66
| Pressure of liquid | 12 | 12 | 11.8 | 11.9 | 11.8 | 11.8 | 11.9 | 12.2 | 11.9 | 11.8 | 11.8 |  | 11.2 | 11.2 | 11.8 | 12 | 12.3 | 12.5 |  | 12.8 | 12.9 | 12.9 | 12.7 | 12.8 | 12.4 | 12.3 | 12.4 | 12.5 | 12.6 | 12.9 | 13 | 13.1 | 12.2 | 12.3 | 12.4 | 12.6 | 12.6 | 12.9 | 13 | 13.3 | 12.8 | 12.7 | 12.6 | 12.6 | 12.5 | 12.3 | 12.2 | 12.2 | 12.2 |  | >17 | >17 | >17 | >17 | >17 |  | 16.5 | 16.5 | 17 | 17 | 17 |  | >17 | >17 | 15.5 | 15.8 |  |  | >17 | >17 | >17 | >17 | 15.8 | 15.2 | 15.2 | 15.8 |  | 16.2 |  |  |  | 16.5 | 16.3 | 16.8
| Pressure in condensor | 13 | 13 | 12.6 | 12.8 | 12.7 | 12.7 | 12.8 | 13 | 12.7 | 12.6 | 12.6 |  | 11.8 | 12 | 12.5 | 12.6 | 13 | 13.3 |  | 13.6 | 13.8 | 13.8 | 13.6 | 13.6 | 13.1 | 13 | 13.2 | 13.2 | 13.4 | 13.2 | 13.4 | 13.4 | 12.5 | 12.6 | 12.8 | 12.9 | 12.9 | 13.3 | 13.3 | 12.9 | 13.1 | 13 | 13 | 13 | 12.9 | 12.7 | 12.6 | 12.6 | 12.6 |  | 12 | 12 | 12 | 12 | 12 |  | 11.5 | 11.5 | 11.8 | 11.8 | 11.8 |  | 11.8 | 11.7 | 11.2 | 11.2 |  |  | 12.2 | 12.2 | 12 | 12 | 11.5 | 11.2 | 11.2 | 11.5 |  | 12 |  |  |  | 12 | 12 | 12
Temperatures
| Temerature at inlet (05.01) | -14.06 | -14.48 | -14 | -13.99 | -14.29 | -14.35 | -13.96 | -14.17 | -13.71 | -13.7 | -13.23 |  | -13.51 | -14.11 | -13.93 | -13.96 | -14.11 | -11.76 |  | -13.45 | -14.05 | -13.91 | -14.05 | -13.91 | -6.17 | -6.181 | -6.07 | -6.036 | -6.482 | -14.29 | -14.33 | -14.34 | -13.86 | -14.08 | -13.94 | -14.02 | -14.13 | -14.24 | -13.91 | -14.01 | -6.665 | -6.309 | -6.281 | -6.598 | -6.454 | -6.292 | -6.565 | -6.776 | -6.209 |  | -6.06 | -5.98 | -5.8 | -12.87 | -6.33 |  | -6.6 | -6.42 | -6.33 | -6.65 | -5.96 |  | -6.2 | -6.59 | -6.26 | -6.5 |  |  | -6.29 | -6.62 | -6.53 | -6.68 | -6.4 | -6.48 | -6.59 | -6.35 |  | -6.4 | -6.5 | -7 |  | -6.04 | -7.27 | -5.16
| Temerature at inlet (05.05) | -15.82 | -16.3 | -15.8 | -15.82 | -16.14 | -16.18 | -16.4 | -16.79 | -16.25 | -16.27 | -15.7 |  | -15.58 | -16.21 | -16.02 | -16.05 | -16.19 | -13.75 |  | -15.31 | -15.97 | -15.83 | -15.99 | -15.86 | -7.896 | -7.746 | -7.724 | -7.729 | -8.146 | -15.99 | -16.03 | -16.06 | -15.68 | -15.94 | -15.83 | -15.87 | -16.01 | -16.12 | -15.78 | -15.91 | -8.474 | -7.557 | -7.64 | -8.14 | -8.04 | -7.746 | -8.279 | -8.452 | -7.907 |  | -8.05 | -8.13 | -8.37 | -16.11 | -8.67 |  | -7.92 | -7.35 | -7.63 | -7.9 | -7.79 |  | -7.8 | -7.77 | -7.58 | -7.83 |  |  | -7.59 | -7.99 | -7.37 | -7.51 | -7.31 | -7.41 | -7.49 | -7.71 |  | -7.44 | -7.5 | -8 |  | -7.43 | -8.51 | -8.31
| Average Temperature at inlet | -14.94 | -15.39 | -14.9 | -14.905 | -15.215 | -15.265 | -15.18 | -15.48 | -14.98 | -14.985 | -14.465 |  | -14.545 | -15.16 | -14.975 | -15.005 | -15.15 | -12.755 |  | -14.38 | -15.01 | -14.87 | -15.02 | -14.885 | -7.033 | -6.9635 | -6.897 | -6.8825 | -7.314 | -15.14 | -15.18 | -15.2 | -14.77 | -15.01 | -14.885 | -14.945 | -15.07 | -15.18 | -14.845 | -14.96 | -7.5695 | -6.933 | -6.9605 | -7.369 | -7.247 | -7.019 | -7.422 | -7.614 | -7.058 |  | -7.055 | -7.055 | -7.085 | -14.49 | -7.5 |  | -7.26 | -6.885 | -6.98 | -7.275 | -6.875 |  | -7 | -7.18 | -6.92 | -7.165 |  |  | -6.94 | -7.305 | -6.95 | -7.095 | -6.855 | -6.945 | -7.04 | -7.03 |  | -6.92 | -7 | -7.5 |  | -6.735 | -7.89 | -6.735 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Temperature after capillaries | -24.12 | -24.94 | -23.79 | -23.8 | -23.94 | -24.37 | -24.08 | -24.58 | -24.09 | -24.2 | -24.48 |  | -23.98 | -23.6 | -23.86 | -23.73 | -23.82 | -23.75 |  | -24.32 | -24.4 | -24.52 | -24.62 | -24.6 | -23.82 | -24.08 | -24.21 | -24.05 | -24 | -24.04 | -24.21 | -24.37 | -23.93 | -24.35 | -23.76 | -24.16 | -23.9 | -24.28 | -24.27 | -24.57 | -23.79 | -23.59 | -23.92 | -24 | -23.34 | -24 | -23.7 | -23.88 | -24.08 |  | -24.2 | -24.33 | -24.26 | -24.77 | -24.77 |  | -24 | -23.9 | -24 | -24.01 | -23.92 |  | -23.3 | -23.4 | -24 | -23.91 |  |  | -24.9 | -23.5 | -23.3 | -23.3 | -23.55 | -23.5 | -23.5 | -24.5 |  | -23.8 |  |  |  | -23.8 | -23.8 | -24
| Temperature at start of capillary 1 | -13.66 | -14.05 | 13.64 | -13.59 | -13.85 | -13.96 | [52 empty] | -8.05
| Ambient temp | 12.864 | 12.83 | 12.875 | 12.953 | 12.986 | 13.142 | 13.655 | 13.778 | 13.739 | 13.8 | 13.8 |  | 17.76 | 17.32 | 17.198 | 17 | 17 | 17 |  | 16.3 | 16.1 | 16 | 16 | 16 | 16.6 | 16.7 | 16.8 | 16.8 | 16.8 | 15.4 | 15.3 | 15.25 | 15.5 | 15.5 | 15.6 | 15.8 | 16.2 | 16.3 | 16.4 | 16.8 | 17.2 | 17.6 | 17.7 | 17.7 | 17.7 | 17.3 | 17.3 | 17.3 | 17.3 |  | 17.74 | 17.62 | 17.45 | 17.31 | 17.4 |  | 14.65 | 14.46 | 14.72 | 14.8 | 15.11 |  | 14.39 | 14.3 | 14.21 | 14.42 |  |  | 14.99 | 14.98 | 14.9 | 14.9 | 14.59 | 15 | 15.2 | 18.11 |  | 17.8 |  |  |  | 18.95 | 18.6 | 18.94
| Temp of vapour after HEX (05.06) | -23.57 | -24.35 | -23.2 | -23.22 | -23.35 | -23.77 | -23.46 | -23.97 | -23.49 | -23.61 | -23.89 |  | -23.52 | -23.15 | -23.4 | -23.3 | -23.38 | -23.3 |  | -23.86 | -23.9 | -24.1 | -24.13 | -24.15 | -23.48 | -23.7 | -23.8 | -23.69 | -23.7 | -23.66 | -23.8 | -24 | -23.6 | -24 | -23.4 | -23 | -23.5 | -23.9 | -24.18 | -24.2 | -23.48 | -23.23 | -23.6 | -23.8 | -23.08 | -23.7 | -23.4 | -23.6 | -23.8 |  | -23.86 | -23.92 | -23.87 | -24.33 | -24.4 |  | -23.57 | -23.57 | -23.66 | -23.6 | -23.5 |  | -23.03 | -23.05 | -23.62 | -23.56 |  |  | -24.57 | -23 | -23 | -23 | -23.2 | -23.1 | -23.1 | -24.07 |  | -23.34 |  |  |  | -23.41 | -23.37 | -23.59
| Temp after Heater (05.04) | 13.67 | 15.054 | 15.3 | 18.2 | 13.06 | 17.987 | 12.4 | 12.448 | 16.187 | 21.04 | 15.66 |  | 17.7 | 13.5 | 15.8 | 12.3 | 14.1 | 15.9 |  | 22 | 17.98 | 19.48 | 22.3 | 21.22 | 23.2 | 26 | 21.8 | 19.7 | 20.8 | 13.4 | 15.03 | 17 | 19 | 20.9 | 21.7 | 18 | 15 | 12.6 | 10.6 | 12.6 | 23.2 | 25.2 | 22.3 | 23.4 | 26.2 | 28.6 | 22.6 | 20.6 | 17 |  | 20.9 | 25.75 | 25.21 | 11.8 | 24.14 |  | 23.68 | 19.51 | 14.63 | 17.6 | 16.93 |  | 16.23 | 18.7 | 13.2 | 15.36 |  |  | 17 | 15.1 | 16.48 | 16 | 18.2 | 16 | 14.3 | 22.01 |  | 16.55 |  |  |  | 21.43 | 20.3 | 25.93
| Temp of liquid before MF (05.23) | 16.238 | 16.49 | 16.3 | 16.339 | 16.5 | 16.8 | 16.748 | 16.462 | 16.384 | 16.457 | 16.457 |  | 20.612 | 20.589 | 20.5 | 20.4 | 20.3 | 20 |  | 18.8 | 18.9 | 18.98 | 19.07 | 19.16 | 19.2 | 19.3 | 19.4 | 19.5 | 19.4 | 17.9 | 17.9 | 18 | 18.7 | 18.9 | 18.9 | 19 | 19.2 | 19.3 | 19.3 | 19.4 | 19.6 | 19.7 | 19.7 | 19.8 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7
| Temp of liquid before PR (05.20) | 14.927 | 14.899 | 15.01 | 14.994 | 15.04 | 15.24 | 15.319 | 15.162 | 14.927 | 15.06 | 15.05 |  | 17.006 | 16.944 | 16.978 | 17 | 17.1 | 17.096 |  | 16.1 | 16.5 | 16.79 | 16.85 | 16.93 | 16.6 | 16.7 | 16.7 | 16.78 | 16.83 | 15.34 | 15.4 | 15.5 | 15.9 | 16 | 16 | 16 | 16.3 | 16.3 | 16.3 | 16.3 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.7 | 16.6 | 16.6 | 16.4 |  | 21.77 | 21.83 | 21.88 | 22.01 | 22.14 |  | 18.77 | 18.84 | 18.94 | 19 | 19 |  | 17.8 | 17.9 | 18.2 | 18.3 |  |  | 18.76 | 18.8 | 18.9 | 18.9 | 19 | 19.1 | 19.2 | 21.3 |  | 21.4 |  |  |  | 22.45 | 22.5 | 22.6
| Temp in condensor | 40 | 39.5 | 38.9 | 38.9 | 38.8 | 39.5 | 40 | 40.5 | 39.8 | 39 | 39 |  | 33 | 33.3 | 36.6 | 37.8 | 38.95 | 37.5 |  | 39.4 | 39.6 | 39.6 | 38.8 | 39 | 37.3 | 37 | 37.5 | 37.8 | 38.2 | 37.8 | 38.3 | 38.5 | 35 | 35.6 | 36.1 | 36.6 | 37.5 | 37.8 | 38.2 | 37.8 | 37.2 | 37 | 37 | 36.7 | 36.3 | 35.5 | 35.4 | 35.4 | 35.7 |  | 33.5 | 33.4 | 33.47 | 33.6 | 32.1 |  | 31.4 | 31.51 | 32.4 | 32.6 | 32.4 |  | 32.5 | 32.2 | 30.2 | 30.4 |  |  | 33.3 | 32.4 | 32.9 | 32.8 | 30.66 | 29.9 | 29.9 | 30.99 |  | 32.08 |  |  |  | 32.54 | 32.42 | 31.93
Massflow
| Massflow | 2.05 | 2.003 | 2.003 | 1.94 | 1.872 | 2.037 | 1.965 | 1.956 | 1.88 | 1.821 | 1.972 | 2.32 | 1.776 | 1.829 | 1.883 | 1.968 | 1.918 | 2.226 |  | 2.265 | 2.349 | 2.273 | 2.176 | 2.228 | 2.1 | 2.03 | 2.14 | 2.21 | 2.29 | 1.552 | 1.523 | 1.477 | 1.455 | 1.423 | 1.384 | 1.474 | 1.521 | 1.569 | 1.609 | 1.659 | 1.58 | 1.54 | 1.497 | 1.451 | 1.425 | 1.313 | 1.345 | 1.395 | 1.452 |  | 2.157 | 2.017 | 2.02 | 2.104 | 1.53 |  | 1.634 | 1.705 | 2.15 | 2.082 | 2.1 |  | 2.275 | 2.24 | 1.6 | 1.77 |  |  | 2.29 | 2.292 | 2.29 | 2.293 | 1.6 | 1.56 | 1.64 | 1.633 | 1.58 | 1.715 | 1.59 | 1.62 |  | 1.615 | 1.655 | 1.735
| Temperature in massflow meter | 10.1 | 10.12 | 10.13 | 10.17 | 10.23 | 10.19 | 10.25 | 10.28 | 10.22 | 10.28 | 10.22 |  | 11.2 | 11.1 | 11.1 | 10.95 | 10.95 | 10.75 |  | 10.45 | 10.44 | 10.52 | 10.58 | 10.6 | 10.69 | 10.8 | 10.73 | 10.73 | 10.7 | 10.5 | 10.53 | 10.58 | 10.87 | 10.92 | 11 | 10.96 | 11.02 | 10.99 | 11 | 10.92 | 11.11 | 11.18 | 11.2 | 11.25 | 11.28 | 11.5 | 11.35 | 11.3 | 11.2 |  | 11.36 | 11.35 | 11.36 | 11.44 | 11.6 |  | 10.07 | 10.13 | 10.32 | 10.3 | 10.36 |  | 9.7 | 9.79 | 9.69 | 9.7 |  |  | 10 | 10 | 10 | 10 | 10.04 | 9.97 | 9.96 | 10.9 |  | 10.1 |  |  |  | 11.5 | 11.48 | 11.5
[65 empty] | 370-400 (11:31-11:37) | 560-580 (12:02-12:06) | 680 - 710 (12:22 - 12:27) |  |  | 385-405 (10:19 -10:23) | 428 - 475 (10:27-10:34) |  | 563 -603 (10:48- 10:55) | 700 (11:11-11:13) | 800 (11:26-11:29) |  | 320 - 340 (17:06 - 17:09) |  | 447 - 488 (5:27 - 5:33) |  |  |  | 590 - 645 (4:33 - 4:43) | 740 - 753 (16:49 -17:01 ) | 986 - 1016(17:39 - 17:44 )
scan range | [57 empty] | 170-180 | 250-260 | 45-60 | 90-110 | 200-220 |  | 250-260
Comments |  |  | 2:46-2:55 change BPR slightly | measure from 2:58 for 10 minutes | 3:08 reduce P to 11bara | 3:22 reduced P to 10.5bara | 3:42 changed pressure to 11.7. 3:58 tried to reduce inlet temp | 16:37 switched in second capillary - massflow very reduced - switched to 3rd capillary | 17:10 reduced pressure to 11.5bar | 17:27 reduce pressure to 11bara, 17:37 tried to get BP correct | 17:45 reduce pressure to 10.5bara | 18:00 pressure up to 11.8bara | 18:10 switched to 4th capillary - massflow higher - not stable at 18:30 - turn system off. | started system running - fixed problem with N6 | 17:57 increased delta pressure to 9bar | 18:16 increased DP to 9.3bar | 18:37 increase DP to 10.0bar | 19:15 reduce DP to 9.5bar | 19:24 swop to cap N10 | 20:30 pump system down and leave for tests tomorrow |  | 14:18 increase DP to 10bar | 14:29 DP down to 9.5bar | 14:44 DP down to 9bar | 14:58 DP upto 9.4bar | test at -7C | 16:20 drop DP to 8.9bar | 16:50 increase DP to 9.6bar | 17:06 DP to 10bar | 17:19 DP to 10.2 | testing N2 0.68 at -15C | drop DP to 10.3bar | 10:31 drop DP to 10bar |  | 14:02 DP to 9.5bar | 14:14 DP to 9bar | 14:24 swop to N7 | 14:36 DP to 9.5bar | 14:56 DP to 10.0 bar | 15:05 DP to 10.4bar | 15:25 DP to 10.7bar | 15:37 T =-7C!!! | 16:03 DP to 10.3bar | 17:14 DP to 10bar | 17:24 DP to 9.5bar | 17:31 DP to 9bar | 17:44 switch to N2 | 18:06 DP to 9.7bar | 18:23 DP to 10.2bar | 18:29 Dp to 10.7bar | pump back in the system | 14:21 swop to N6 | 14:30 swop to N8 | 14:40 change temp to -15C | 15:09 change to N2, -7C | 15:30 close off system and shorten capillary |  | 14:37 swoped to N7, vapour heater at 53V | 14:50 swop to N1 | 15:16 swop to N6, heater at 58V | 15:24 swop to N8 |  |  | 100-200 10:50-11:05 temp too high | N6 at 11:13 | N2 at 11:37, WRONG as same massflow as before!! | N7, 0.68 at 12:07 | massflow > 2.3 not fully tested |  | have reference! Need to measure at 1.7bara BP | 10:35, swop to N6, 0.75 |  | have second reference capillary! | 10:56 swop to N2, 0.68, same result as before, don’t understand why not more massflow! | 11:13 swop to N10, 0.68 | 11:29 swop to N8, 0.68 | 17:10 swop to N10, 0.68 |  | 17:34 swop to N10 | 17:35 swop to N2 |  |  | 16:44 swop to N2, 0.68 | 17:01 swop to N8, 0.68
VQ inlet |  | 9.938% | 10.29% | 9.641% | 9.646% | 9.455% | 9.844% | 9.637% | 9.828% | 9.864% | 9.972% | 10.82% |  | 10.22% | 9.162% | 9.632% | 9.465% | 9.401% | 11.93% |  | 10.75% | 10.15% | 10.43% | 10.37% | 10.49% | 18.2% | 18.53% | 18.73% | 18.59% | 18.08% | 9.639% | 9.771% | 9.915% | 9.927% | 10.1% | 9.626% | 9.974% | 9.57% | 9.844% | 10.2% | 10.38% | 17.59% | 18.08% | 18.38% | 18.02% | 17.49% | 18.4% | 17.66% | 17.63% | 18.43% |  | 18.55% | 18.68% | 18.58% | 11.09% | 18.63% |  | 18.13% | 18.44% | 18.44% | 18.13% | 18.47% |  | 17.72% | 17.63% | 18.5% | 18.15% |  |  | 19.36% | 17.59% | 17.78% | 17.62% | 18.13% | 17.98% | 17.88% | 18.88% |  | 18.3% | -8.668% | -9.287% |  | 18.51% | 17.25% | 18.7%
VQ outlet |  | 9.938% | 10.29% | 9.641% | 9.646% | 9.455% | 9.844% | 9.637% | 9.828% | 9.864% | 9.972% | 10.82% |  | 10.22% | 9.162% | 9.632% | 9.465% | 9.401% | 11.93% |  | 10.75% | 10.15% | 10.43% | 10.37% | 10.49% | 18.2% | 18.53% | 18.73% | 18.59% | 18.08% | 9.639% | 9.771% | 9.915% | 9.927% | 10.1% | 9.626% | 9.974% | 9.57% | 9.844% | 10.2% | 10.38% | 17.59% | 18.08% | 18.38% | 18.02% | 17.49% | 18.4% | 17.66% | 17.63% | 18.43% |  | 18.55% | 18.68% | 18.58% | 11.09% | 18.63% |  | 18.13% | 18.44% | 18.44% | 18.13% | 18.47% |  | 17.72% | 17.63% | 18.5% | 18.15% |  |  | 19.36% | 17.59% | 17.78% | 17.62% | 18.13% | 17.98% | 17.88% | 18.88% |  | 18.3% | -8.668% | -9.287% |  | 18.51% | 17.25% | 18.7%
Hliq_sat |  | 173.9399 | 173.0291 | 174.3064 | 174.2953 | 174.1398 | 173.6622 | 173.9843 | 173.429 | 173.9732 | 173.8511 | 173.5401 |  | 174.0954 | 174.5175 | 174.2287 | 174.3731 | 174.2731 | 174.3509 |  | 173.7178 | 173.6289 | 173.4956 | 173.3846 | 173.4068 | 174.2731 | 173.9843 | 173.84 | 174.0177 | 174.0732 | 174.0288 | 173.84 | 173.6622 | 174.1509 | 173.6845 | 174.3398 | 173.8955 | 174.1843 | 173.7622 | 173.7733 | 173.4401 | 174.3064 | 174.5286 | 174.1621 | 174.0732 | 174.8063 | 174.0732 | 174.4064 | 174.2065 | 173.9843 |  | 173.8511 | 173.7067 | 173.7844 | 173.218 | 173.218 |  | 174.0732 | 174.1843 | 174.0732 | 174.0621 | 174.1621 |  | 174.8507 | 174.7396 | 174.0732 | 174.1732 |  |  | 173.0736 | 174.6285 | 174.8507 | 174.8507 | 174.573 | 174.6285 | 174.6285 | 173.5179 |  | 174.2953 | 200.73 | 200.73 |  | 174.2953 | 174.2953 | 174.0732
Hvap_sat |  | 276.5345 | 276.0621 | 276.7246 | 276.7188 | 276.6382 | 276.3904 | 276.5575 | 276.2695 | 276.5518 | 276.4884 | 276.3271 |  | 276.6151 | 276.834 | 276.6843 | 276.7591 | 276.7073 | 276.7476 |  | 276.4192 | 276.3732 | 276.304 | 276.2464 | 276.2579 | 276.7073 | 276.5575 | 276.4826 | 276.5748 | 276.6036 | 276.5806 | 276.4826 | 276.3904 | 276.6439 | 276.402 | 276.7419 | 276.5114 | 276.6612 | 276.4423 | 276.4481 | 276.2752 | 276.7246 | 276.8398 | 276.6497 | 276.6036 | 276.9838 | 276.6036 | 276.7764 | 276.6727 | 276.5575 |  | 276.4884 | 276.4135 | 276.4538 | 276.16 | 276.16 |  | 276.6036 | 276.6612 | 276.6036 | 276.5978 | 276.6497 |  | 277.0069 | 276.9493 | 276.6036 | 276.6554 |  |  | 276.0851 | 276.8917 | 277.0069 | 277.0069 | 276.8628 | 276.8917 | 276.8917 | 276.3155 |  | 276.7188 | 290.43 | 290.43 |  | 276.7188 | 276.7188 | 276.6036
Hdiff_sat |  | 102.5946 | 103.0329 | 102.4181 | 102.4235 | 102.4983 | 102.7282 | 102.5732 | 102.8405 | 102.5785 | 102.6373 | 102.787 |  | 102.5197 | 102.3166 | 102.4556 | 102.3861 | 102.4342 | 102.3967 |  | 102.7015 | 102.7442 | 102.8084 | 102.8619 | 102.8512 | 102.4342 | 102.5732 | 102.6427 | 102.5571 | 102.5304 | 102.5518 | 102.6427 | 102.7282 | 102.493 | 102.7175 | 102.4021 | 102.6159 | 102.4769 | 102.6801 | 102.6747 | 102.8351 | 102.4181 | 102.3112 | 102.4876 | 102.5304 | 102.1776 | 102.5304 | 102.37 | 102.4662 | 102.5732 |  | 102.6373 | 102.7068 | 102.6694 | 102.942 | 102.942 |  | 102.5304 | 102.4769 | 102.5304 | 102.5357 | 102.4876 |  | 102.1562 | 102.2096 | 102.5304 | 102.4823 |  |  | 103.0115 | 102.2631 | 102.1562 | 102.1562 | 102.2898 | 102.2631 | 102.2631 | 102.7977 |  | 102.4235 | 89.7 | 89.7 |  | 102.4235 | 102.4235 | 102.5304
Hliq_end_cap |  | 184.1361 | 183.6363 | 184.1806 | 184.175 | 183.8307 | 183.7752 | 183.8696 | 183.5364 | 184.0917 | 184.0862 | 184.6637 |  | 184.5749 | 183.8918 | 184.0973 | 184.0639 | 183.9029 | 186.563 |  | 184.7581 | 184.0584 | 184.2139 | 184.0473 | 184.1972 | 192.9184 | 192.9956 | 193.0695 | 193.0856 | 192.6063 | 183.914 | 183.8696 | 183.8474 | 184.325 | 184.0584 | 184.1972 | 184.1306 | 183.9918 | 183.8696 | 184.2417 | 184.1139 | 192.3226 | 193.0295 | 192.999 | 192.5453 | 192.6808 | 192.934 | 192.4864 | 192.2731 | 192.8907 |  | 192.894 | 192.894 | 192.8607 | 184.636 | 192.3998 |  | 192.6663 | 193.0828 | 192.9773 | 192.6497 | 193.0939 |  | 192.9551 | 192.7552 | 193.044 | 192.7718 |  |  | 193.0217 | 192.6163 | 193.0106 | 192.8496 | 193.1162 | 193.0162 | 192.9107 | 192.9218 |  | 193.044 | 192.9551 | 192.3998 |  | 193.2494 | 191.9666 | 193.2494
| Capillary order | [17 empty] | reduced condensor set temp from 43 to 40
|  | N1 | N6 | N8 | N10 | N5 |  | N2 | N7 |  | N8 | N10 | [43 empty] | Cut 0.75mm ID to 3.2m
| nominal ID | 0.76 | 0.76 | 0.76 | 0.76 | 0.68 |  | 0.68 | 0.68 |  | 0.68 | 0.68 | [43 empty] | Cut 0.68mm ID to 3.2m
| length | 3.44 | 3.446 | 3.4455 | 2.63 | 3.448 |  | 3.4 | 3.444 |  | 3.2 | 3.2
| measured ID | 0.743 | 0.742 | 0.746 | ? | 0.687 |  | 0.678 | 0.689 |  | 0.688 | 0.686
|  |  | NEED to check length of N6 |  |  | not tested
28/02/2005
| new capillary lengths | 3.2 | 3.198 | 3.2 | ---- |  |  | 3.2 | 3.2
| 2005-01-03 | 2.9 | 2.75 | 2.75 | ---- |  |  | 3.1 | 3.1
2005-02-03
|  | ----- | 2.65 | 2.72 | ---- |  |  | 3.1 | ---- |  | 3.2 | 3.2
| 2/3/2005 pm | [6 empty] | 3 |  |  | 3.12 | 3.05
| 2005-03-03 | [6 empty] | 2.92 |  |  | 3.1 | 2.97

## summary of 0.76
from summary data
the fit for massflow as a function of length is taken for -10C and DP=11.3bar
therefore taken linear fit to new data to get DP=11.3bar
the temperature here is -15C so massflow is higher than for the fit where T=-10C
if massflow reduced by 10% then length is closer to 3m!
| name | N1 | N1 | N8 | N6 | N10 | N10 -7C | N1, 0.76 | N6, 0.76 | N8, 0.76 | N8, 0.76 | N2, 0.68
| ID | 0.743 | 0.743 | 0.746 | 0.742 |  |  | 0.76 | 0.76 | 0.76 | 0.76 | 0.68
| length | 3.44 | 3.44 | 3.4455 | 3.446 | 2.63 | 2.63 | 3.44 | 3.446 | 3.446 | 3.446 | 3.4 |  | so old cap at length 3.44 has massflow
| Temp | -15 | -15 | -15 | -15 | -15 | -7 | -7.055 | -7.055 | -7.085 | -14.49 | -7.5 |  | 3.44 | 1.7919
| massflow | 2.29 | 2.18 | 2.12 | 2.1209 | 2.5156 | 2.4093 | 2.157 | 2.017 | 2.02 | 2.104 | 1.53 |  | 2.63 | 2.0912
| pressure | 12.2 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.4 | 11.45 | 11.44 | 11.44 | 11.54
| diff |  |  | 2.752% | [12 empty] | N1 | N8 | N6 | N10
| massflow = 3.6479 x length ^ (-0.5754) | [12 empty] | we have massflow = |  |  | 2.071 | 2.014 | 2.0149 | 2.3898
| length for 2.29 |  | 2.4467 | 2.5683 | [9 empty] | corrected for Tdiff
factor of 0.95 in massflow
| length for T=-10C, m=2.1755 | [12 empty] | so diff in massflow = |  |  | 0.27913 | 0.22213 | 0.22298 | 0.29863
|  |  | 2.6748 | 2.8077 | [9 empty] | at -10C
[17 empty] | N1 | N8 | N6 | N10
[14 empty] | not corrected for Tdiff |  | m= | 2.18 | 2.12 | 2.1209 | 2.5156
length (m) | m for old cap |  | m for new cap at -10C |  |  |  | m new cap at -15C |  |  |  | new caps at -7C |  |  | diff in massflow, -15C= |  |  | 0.38813 | 0.32813 | 0.32903 | 0.42441
|  |  | N1 | N8 | N6 | N10 | N1 | N8 | N6 | N10 | N1 | N8 | N6
1 | 3.6479 |  | 3.927 | 3.87 | 3.8709 | 3.9465 | 4.036 | 3.976 | 3.9769 | 4.0723 | 4.013 | 3.873 | 3.876 | ratios, -15C to -7C |  | diff in massflow 3.44, -7C and old cap
2 | 2.4481 |  | 2.7272 | 2.6702 | 2.6711 | 2.7467 | 2.8362 | 2.7762 | 2.7771 | 2.8725 | 2.8132 | 2.6732 | 2.6762 | N1 | 0.98945 | 0.36513
3 | 1.9387 |  | 2.2178 | 2.1608 | 2.1617 | 2.2373 | 2.3268 | 2.2668 | 2.2677 | 2.3631 | 2.3038 | 2.1638 | 2.1668 | N6 | 0.95101 | 0.22513
4 | 1.6429 |  | 1.9221 | 1.8651 | 1.8659 | 1.9415 | 2.0311 | 1.9711 | 1.972 | 2.0673 | 2.0081 | 1.8681 | 1.8711 | N8 | 0.95283 | 0.22813
3.44 | 1.7919 |  | 2.071 | 2.014 | 2.0149 | 2.0905 | 2.18 | 2.12 | 2.1209 | 2.2163 | 2.157 | 2.017 | 2.02 | about 5% increase in going to -15C from -7C
2.45 | 2.1783 |  | 2.4574 | 2.4004 | 2.4013 | 2.4769 | 2.5664 | 2.5064 | 2.5073 | 2.6027 | 2.5434 | 2.4034 | 2.4064
2.5 | 2.1531 |  | 2.4322 | 2.3752 | 2.3761 | 2.4517 | 2.5412 | 2.4812 | 2.4821 | 2.5775 | 2.5182 | 2.3782 | 2.3812
2.6 | 2.1051 |  | 2.3842 | 2.3272 | 2.3281 | 2.4037 | 2.4932 | 2.4332 | 2.4341 | 2.5295 | 2.4702 | 2.3302 | 2.3332
2.7 | 2.0599 |  | 2.339 | 2.282 | 2.2828 | 2.3585 | 2.448 | 2.388 | 2.3889 | 2.4843 | 2.425 | 2.285 | 2.288
2.8 | 2.0172 |  | 2.2963 | 2.2393 | 2.2402 | 2.3158 | 2.4053 | 2.3453 | 2.3462 | 2.4416 | 2.3823 | 2.2423 | 2.2453
2.9 | 1.9769 |  | 2.256 | 2.199 | 2.1999 | 2.2755 | 2.365 | 2.305 | 2.3059 | 2.4013 | 2.342 | 2.202 | 2.205
2.95 | 1.9575 |  | 2.2367 | 2.1797 | 2.1805 | 2.2562 | 2.3457 | 2.2857 | 2.2866 | 2.3819 | 2.3227 | 2.1827 | 2.1857
3 | 1.9387 |  | 2.2178 | 2.1608 | 2.1617 | 2.2373 | 2.3268 | 2.2668 | 2.2677 | 2.3631 | 2.3038 | 2.1638 | 2.1668
3.1 | 1.9025 |  | 2.1816 | 2.1246 | 2.1254 | 2.2011 | 2.2906 | 2.2306 | 2.2315 | 2.3269 | 2.2676 | 2.1276 | 2.1306
3.2 | 1.868 |  | 2.1471 | 2.0901 | 2.091 | 2.1666 | 2.2561 | 2.1961 | 2.197 | 2.2924 | 2.2331 | 2.0931 | 2.0961
3.3 | 1.8352 |  | 2.1144 | 2.0574 | 2.0582 | 2.1339 | 2.2234 | 2.1634 | 2.1643 | 2.2596 | 2.2004 | 2.0604 | 2.0634
[20 empty] | 2.4961 | Cap N6 | 2.2142
| N1 | N6 | N8 | [17 empty] | Cap N8 | 2.3155
3.44 | 2.157 | 2.017 | 2.02 | [17 empty] | Cap N1 | 2.5577
3.2 | 2.15 | 2.082 | 2.1
2.9 | 2.35
2.75 |  | 2.24 | 2.275
2.72 |  |  | 2.292
2.65 |  | 2.293

## summary of 0.68
sample | N2 | N7 | N2 | N7
ID | 0.681 | 0.693 | 0.681 | 0.693
length | 3.4 | 3.444 | 3.4 | 3.444
temperature | -15C | -15C | -7C | -7C
massflow | 1.6143 | 1.6986 | 1.5132 | 1.6258
pressure | 11.3 | 11.3 | 11.3 | 11.3
target massflow = 1.74g/s
massflow at -7C
length N2 | N2 | length N7 | N7 | N10 - length | N10 | N8 - length | N8 | length of old cap | massflow | prediction N2 | prediction N7
3.4 | 1.53 | 3.444 | 1.6258 |  |  |  |  | 3.44 | 1.7919 | 1.5197 | 1.6258
3.2 |  | 3.2 | 1.705 | 3.2 | 1.56 | 3.2 | 1.64 | 3.4 | 1.804 | 1.53 | 1.6367
3.1 | 1.6 | 3.1 | 1.77 | 3.05 | 1.59 | 3.12 | 1.715 | 3.2 | 1.868 | 1.5843 | 1.6949
3 | 1.62 | 3 |  | 2.97 | 1.615 | 3.1 | 1.735 | 3.1 | 1.9025 | 1.6135 | 1.7261
2.92 | 1.655 | [6 empty] | 3 | 1.9387 | 1.6443 | 1.759
[8 empty] | 2.9 | 1.9769 | 1.6766 | 1.7936
| N2 | N7 | N10 | N8 |  |  |  | 2.8 | 2.0172 | 1.7108 | 1.8302
% of required | 95.11% | 101.7% | 92.82% | 99.71% |  |  |  | 2.7 | 2.0599 | 1.747 | 1.8689
[8 empty] | 2.6 | 2.1051 | 1.7854 | 1.9099
[8 empty] | 2.5 | 2.1531 | 1.8261 | 1.9535
ratio of 3.44 |  |  |  | 2 | 1.8966 | 1.74
for N7 | 0.9073 |  |  | 3.7 | 1.8966 | 1.74
ratio of 3.4
for N2 | 0.84813
total of the 2 0.68 |  |  | length N2 | N2
3.37 |  |  | 3.4 | 14.46 | [6 empty] | N10 | N8 | N2 | From fits what is length for massflow = |  | 1.8966 | g/s
want |  |  | 3.2 | 14.8 | [5 empty] | y | 1.56 | 1.64 | 1.6 |  | length
3.48 | [9 empty] | x | 3.2 | 3.2 | 3.1 | Cap N2 | 2.2041
[10 empty] | a | 0.9456 | 0.9456 | 0.9456 | Cap N7
[10 empty] | b | -6.6073 | -6.6073 | -6.6073 | Cap N8
[10 empty] | c | 13.0204 | 13.1004 | 12.9954 | Cap N10 | 2.0821
2 | 1.9906 | 2.16
2.5 | 1.7814 | 1.9508 | [7 empty] | y=1.74
3 | 1.6269 | 1.7963 | [7 empty] | x= | 2.9678 | 3.0555 | 2.9432
3.1 | 1.6005 | 1.77
3.5 | 1.5067 | 1.6762 | [7 empty] | x = {-b +- sqrt ( b^2 - 4ac) }/2a
4 | 1.4099 | 1.5793

## 0.76 lengths we have
have length cut off | length | spool | 0.76 | 0.3 | 3.5 | 3.5 | 3.3 | 3.1 | 0.9
|  |  | org length | -30cm for ends | take off used sections | number of caps at 3.5m | number of caps at 3.3m | number of caps at 3.1m | barrel caps at 0.9m
* | 1 | 1 | 32 | 31.7 | 28.2 | 8 | 8 | 9 |  | 31.3333 | 8.5455
* | 1 | 2 | 20 | 19.7 | 16.2 | 4 | 4 | 5 |  | 18 | 4.9091
* | 1 | 3 | 44.8 | 44.5 | 41 | 11 | 12 | 13 |  | 45.5556 | 12.4242
* | 1 | 4 | 46 | 45.7 | 42.2 |  |  |  | 46 | 46.8889 | 12.7879
* | 1 | 5 | 45 | 44.7 | 41.2 | 11 | 12 | 13 |  | 45.7778 | 12.4848
* | 1 | 6 | 46 | 45.7 | 42.2 |  |  |  | 46 | 46.8889 | 12.7879
* | 1 | 7 | 27 | 26.7 | 23.2 | 6 | 7 | 7 |  | 25.7778 | 7.0303
* | 1 | 8 | 37 | 36.7 | 33.2 | 9 | 9 | 9 |  |  | 10.0606
* | 1 | 9 | 45 | 44.7 | 41.2 | 11 | 12 | 13 |  | 45.7778 | 12.4848
* | 1 | 10 | 26 | 25.7 | 22.2 | 6 | 6 | 6 |  |  | 6.7273
* | 1 | 11 | 45 | 44.7 | 41.2 | 11 | 12 | 13 |  | 45.7778 | 12.4848
* | 1 | 12 | 45 | 44.7 | 41.2 | 11 | 12 | 13 |  | 45.7778 | 12.4848
[5 empty] | total number of caps | 88 | 94 | 101 | 92
[5 empty] | total required inc 10% spare | 88 | 88 | 88 | 97
[5 empty] | excess | 0 | 6 | 13 | -5
require 88 good barrel caps
[5 empty] | 10% spare = 97 |  |  |  | 97
total we have
If cut off 3.3 then how much length left | 0.9
how many barrel caps?
1.8 | 2
3 | 3
1.4 | 1
42.2 | 46
1.6 | 1
42.2 | 46
0.1 | 0
3.5 | 3
1.6 | 1
0 | 0
1.6 | 1
1.6 | 1
barrel caps | 105
If barrel cap = 0.9m
then 88 caps = | 79.2
equi to EC caps (EC cap = 3.3m) | 24
equi to EC caps (EC cap = 3.5m) | 22.6286

## 0.68 lengths we have
|  | 0.3 | 3.5 | 3.5 | 3.3 | 3.1
spool | org length | -30cm for ends | take off used sections | number of caps at 3.5m | number of caps at 3.3m | number of caps at 3.1m
1 | 45.1 | 44.8 | 41.3 | 11 | 12 | 13
2 | 50.1 | 49.8 | 46.3 | 13 | 14 | 14
3 | 45 | 44.7 | 41.2 | 11 | 12 | 13
4 | 51 | 50.7 | 47.2 | 13 | 14 | 15
5 | 50.2 | 49.9 | 46.4 | 13 | 14 | 14
6 | 48 | 47.7 | 44.2 | 12 | 13 | 14
7 | 50.3 | 50 | 46.5 | 13 | 14 | 15
8 | 50.4 | 50.1 | 46.6 | 13 | 14 | 15
9 | 43 | 42.7 | 39.2 | 11 | 11 | 12
10 | 50.5 | 50.2 | 46.7 | 13 | 14 | 15
|  |  | Total num of caps | 123 | 132 | 140
|  |  | Require in 10% spare | 141 | 141 | 141
|  |  | Difference | -18 | -9 | -1

## change in massflow
Length (m) | Massflow (g/s) | Delta L (cm) | Delta M | %increase | %increase for 10cm if linear
0.68 capillary - target massflow was 1.74
3.05 | 1.59 | 8 | 0.025 | 1.572% | 1.965%
2.97 | 1.615
3.12 | 1.715 | 2 | 0.02 | 1.166% | 5.831%
3.1 | 1.735
3 | 1.62 | 8 | 0.035 | 2.16% | 2.701%
2.92 | 1.655
3.2 | 1.705 | 10 | 0.065 | 3.812% | 3.812%
3.1 | 1.77
0.76 capillary - target massflow was 2.29
3.2 | 2.15 | 30 | 0.2 | 9.302% | 3.101%
2.9 | 2.35
2.75 | 2.24 | 10 | 0.053 | 2.366% | 2.366%
2.65 | 2.293
2.75 | 2.275 | 3 | 0.017 | 0.7473% | 2.491%
2.72 | 2.292