## Sheet1
Prediction of Barrel Capillaires!
capillary measured is -.75mm ID
Pressure = 13bara before and 1.74bara after
Temperature of liquid before capillary = -10C
Range of lengths give in table with masflow measured
Question is which fit do you think is more physical?
capillary length | massflow at -10C
1.5 | 2.869
2 | 2.46
2.5 | 2.17
3 | 1.937
4 | 1.635
solution of quadratic
T=-10C |  | massflow= | 3.9
0.1346 | a | 0.1346
-1.228 | b | -1.228
4.3978 | c | 0.4978
| l= | 0.15759
0.0077032
solution of power
T=-10C
y=ax^b | massflow = | 3.9
a | 3.6479
b | -0.5754
x= | 0.89035
from barrel, capillary = 0.76mm
T=-17C
length | massflow
0.9 | 3.835
0.75 | 4.435

## Sheet2
ID | 0.65 -old | 0.75 -old | 1 -old | .75 -second
length | 0.6551 | 0.7421 | 0.9987 | 0.7441
6 | 0.9968 |  | 3.095
5.144 | 1.0331
4.14 | 1.2399 |  |  | 1.147
3.023 | 1.4486 | 2.0657 | 4.4801 | 1.353
2.13 | 1.6889
NEW measurements in August 2004
ID | 0.65_aug | 0.75 | 0.9 | 1_aug
length
1.5 | 2.181
2 | 1.875 |  |  | 5.26
Prediction of Barrel Capillaires!
from 0.75 fit of massflow agains T for P=13bara and l =3m
massflow = grad * T + c
grad= | -0.0141 | c= | 1.9247
length | massflow at -10C | c' | predicted flow +12C | % less
1.5 | 2.869 | 2.728 | 2.5588 | 10.81%
2 | 2.46 | 2.319 | 2.1498 | 12.61%
2.5 | 2.17 | 2.029 | 1.8598 | 14.29%
3 | 1.937 | 1.796 | 1.6268 | 16.01%
4 | 1.635 | 1.494 | 1.3248 | 18.97%
solution of quadratic
T=+12C |  | massflow= | 3.9 | T=10C |  | massflow= | 3.9
0.1346 | a | 0.1346 |  | 0.1346 | a | 0.1346
-1.228 | b | -1.228 |  | -1.228 | b | -1.228
4.0876 | c | 0.1876 |  | 4.3978 | c | 0.4978
| l= | 0.16247 |  |  | l= | 0.15759
|  | 0.0028157 |  |  |  | 0.0077032
solution of power
T=+12C |  |  |  | T=10C
y=ax^b | massflow = | 3.9 |  | y=ax^b | massflow = | 3.9
a | 3.4021 |  |  | a | 3.6479
b | -0.6731 |  |  | b | -0.5754
x= | 0.81635 |  |  | x= | 0.89035
from barrel, capillary = 0.76mm
T=-17C
length | massflow
0.9 | 3.835
0.8 | 4.435