# Recent results from cooling tests at RAL

Version of 30/8/02. Still PRELIMINARY

## Steve Snow, Ian Wilmut

In recent months we have used the C3F8 evaporative cooling rig at RAL to test prototype cooling structures, to measure the heat transfer coefficient (HTC) and to test an irradiated module.

## The Cooling Cycle

In the cooling cycle C3F8 is compressed to a liquid, cooled to room temperature, then further cooled before it is injected into a capillary. At input to the capillary its pressure is around 5.5 bar and its temperature is around –15 C. During its passage down the capillary its pressure drops to around 1.5 to 2 bar, which is just below the saturated vapour pressure, so shortly before reaching the end of the capillary it is ready to boil. Then it enters a tube of around 4mm ID and passes through the Geneva module test box (if present) then through a series of cooling blocks and finally through a pair of instrumented copper blocks which measure the heat transfer coefficient. The capillary and all of these test structures are in a freezer. The fluid then passes to a collection tank at room temperature, which is at the input to the compressor. The compressor speed is governed by a controller so as to maintain a constant pressure in the collection tank.

## Test structures and run conditions.

The following runs were used:

Run 2. A series of 5 baseline carbon blocks on a copper nickel pipe were tested. The carbon blocks were insulated from the freezer environment but the copper blocks were not insulated so we ignore the HTC data from this run. Coolant at –26 C.

Run 3. Nominally the same as Run 2. Results were slightly different so we average together Runs 2 and 3.

Run 6. A series of four fully split blocks, two made from carbon and two from aluminium. Pipe from copper nickel. Coolant at –25 C. Copper blocks insulated so we use HTC data from now on.

Run 7. Same structure as Run 6 but coolant at –20 C.

Run 8. The structure of Run 6 was modified by adding a filler of thermally conductive glue on to the back of the cooling blocks. Coolant at –20 C.

Run 9. An irradiated inner module (K5-313) was run in the Geneva module box at a range of coolant temperatures from –20 to –13 C. The rest of the test structure was also

powered on, so flow conditions should be the same as in Runs 6 to 8.

## Heat Transfer Coefficient.

The heat transfer coefficient is measured by passing the fluid through a heated and instrumented copper block with a simple geometry. The copper nickel pipe has 4mm OD and 70 micron wall thickness. It is soldered into a copper block with a square 20x20 mm cross section. The block length is 40 mm giving a total contact area of 4.85 cm2 ignoring end effects. Heaters are glued on to two opposite sides of the block and temperature sensors are glued onto the centres of the other two sides. This geometry ensures that the sensor temperature is very close to the pipe wall temperature. A simulation showed that the difference between the sensor temperature and the average pipe wall temperature should be 0.023 Kelvin per Watt of heating, which is so small that we ignore it.

There were pressure sensors on both sides of the copper block and there was a temperature sensor on the pipe at the upstream side. We found that both pressure sensors gave very steady readings and were always close to 0.1 bar above the pressure set at the compressor input. When no power is applied to the heaters we find that the temperature of the block and the of nearby pipe is within 0.3 degrees of the temperature derived from the pressure readings via the relation below which is a fit to the data in [1]:

T = -65.55 + 37.403 P – 9.9686 P2 + 1.2672 P3

However, when power is applied to the heaters we find that the pipe temperature sensor gets warmer even though the pressure sensors do not change. The pipe sensor is too far from the block to be directly influenced by heat flowing along the pipe walls, so we assume that it is picking up some heat by convection through the air. Therefore we use the temperature derived from pressure measurement as our measure of the fluid temperature inside the pipe.

Convection could also have an influence on the copper block temperature sensors. We have minimised this by gluing a section of the pt100 lead onto the block and by insulating the whole region from the freezer environment. Before these precautions were taken we were finding HTC values up to 25 % higher than the results reported here. We guess that our improvements have reduced systematic errors caused by convection by at least a factor of two but this is only an estimate. Our results are shown in Figure 1, together with a linear fit. The same data is plotted in Figure 2 as a function of temperature difference.

Runs 7 and 8 gave very similar results even though they were taken at somewhat different temperatures, while Run 6 gave slightly lower values of HTC at high power density. There is no reason to prefer one run to another so we fit all together. The fit result will be used in simulations of the cooling blocks.

Figure 1. Heat Transfer Coefficient versus power density.

Figure 2. Heat Transfer Coefficient versus block-fluid temperature difference.

## Block Tests.

### Results

Figures 3 to 5 show the temperatures measured on prototype cooling blocks, relative to the coolant temperature. In each case the detector part and the hybrid part of each block are measured separately and are plotted in adjacent channels, so channels 1 and 2 are the detector and hybrid parts of block 1, channels 3 and 4 are the detector and hybrid parts of block 2, etc. Four extreme loads are plotted from the nine loads that were recorded. The key shows the loads in the form hybrid+detector power. All five baseline blocks behaved rather similarly, though the fourth is distinctly worse than the others. The average of the five blocks is shown in Table 1 for all loads. The split blocks are less uniform. This may be partly because the two on the left were made from carbon and the other two from aluminium. However, they are not dramatically different so we average all four together and show the result in Table 1. Surprisingly, Run 8 shows that the back filled split blocks were no better than the unfilled version. This must indicate that the epoxy that we used to fill them did not have a very high conductivity. Note that the hybrid sensor on the second block was detached in this run so it should be ignored.

Figure 3. The temperatures of five baseline carbon blocks relative to the coolant.

Figure 4. The temperatures of four split blocks relative to the coolant.

Figure 5. The temperatures of four split and filled blocks relative to the coolant.

#### Discussion.

As expected, the split has a beneficial effect on the detector temperature at low detector powers, at the expense of increasing the hybrid temperature. However, at the highest power both detector and hybrid get hotter as a result of the split. This is hard to understand. If one thinks of the block as a network of thermal resistances and splitting it corresponds to making one of the resistors infinite, then the temperatures on the two sides of the split must diverge from their un-split values. In other words, if the hybrid gets hotter then the detector should necessarily get cooler. The reason(s) for the breakdown of this simple picture may be:

- The split blocks may not have been as well made as the baseline version.

- Measurement errors of order 1 degree, caused by the effect of the environment on the sensors, could have obscured the benefit of the split.

- The split is really a distributed object. Representing it by a single resistance may be unrealistic.

- One of the dominant resistances in the system is the heat transfer coefficient which is non linear.

Whatever the reason it is clear that, unless we find a major flaw in the way these split blocks were made, there is not much to be gained in detector temperature by splitting the block.

| Hybrid Power | Detector Power | Baseline Hybrid Temperature | Baseline Detector Temperature | Split Hybrid Temperature | Split Detector Temperature |
| --- | --- | --- | --- | --- | --- |
| 0 | 0 | 0.3 (0.0) | 0.3 (0.0) | 0.1 (0.0) | 0.9 (0.0) |
| 0 | 1 | 2.1 (1.8) | 2.5 (2.4) | 0.4 (0.2) | 3.6 (4.1) |
| 0 | 2 | 4.2 (3.5) | 4.8 (4.5) | 2.0 (0.4) | 8.9 (7.5) |
| 3.5 | 0 | 8.2 (7.4) | 7.1 (5.5) | 12.8 (10.5) | 3.4 (0.6) |
| 3.5 | 1 | 9.4 (8.6) | 8.6 (7.3) | 13.8 (10.6) | 7.7 (4.6) |
| 3.5 | 2 | 10.2 (9.6) | 9.7 (8.9) | 14.6 (10.6) | 11.4 (7.8) |
| 7 | 0 | 11.7 (12.8) | 9.7 (9.2) | 19.2 (16.5) | 5.1 (0.9) |
| 7 | 1 | 12.4 (13.6) | 10.7 (10.5) | 20.3 (16.6) | 9.4 (4.8) |
| 7 | 2 | 12.8 (14.3) | 11.4 (11.8) | 20.7 (16.6) | 12.5 (8.0) |

Table 1. Average temperatures of the blocks relative to the coolant for the nine loads and two block types. Measured values are on the left followed by simulated values in brackets.

#### Block Simulations.

We have simulated the two versions of the cooling block with an FEA model in FlexPDE. The geometry of the real block has been greatly simplified in the model. The model does include the effects of conduction in the carbon material ( assumed to be 200,200,50 W/m.K ) , conduction in the pipe wall (30 W/m.K) and the power dependent heat transfer coefficient taken from the fit in Figure 1. Simulation results are reported in Table 1 and Figures 5 and 6. It can be seen that the simulation predicts a more effective split than we measure in reality. The simulated temperatures are in reasonable agreement with the measurements for the baseline block but lower than the measurements for the split block. It has hard to see how this pattern can be a result of the simplified geometry of the simulation.

Figure 5. The baseline block data from Table 1 is plotted versus the nine load conditions from 0+0 W to 7+2 W.

Figure 6. The split block data from Table 1 is plotted versus the nine load conditions from 0+0 W to 7+2 W.

## Module Tests.

The experimental details and first results from the module test apparatus are described in [2]. After the experiments described in [2] the module was left on the baseline cooling block with good thermal contact established and we did not move it from there. Between the first tests and our tests the module spent about two weeks at room temperature so it will have experienced further annealing and we expect the detector leakage current to have dropped.

Our aim was turn up the coolant temperature and the environment temperature until we observed thermal runaway of the detector leakage current and then to derive from this data the safety factor that the module would have if run at a lower coolant temperature such as –20 C. In fact we did not produce thermal runaway so we can only derive a lower limit on this safety factor.

| Run | 9a | 9b | 9c | 9d | 9e | 9f | 9g |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Hybrid power (W) | 0 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 |
| Detector current (uA) | 206 | 489 | 583 | 653 | 740 | 950 | 614 |
| Detector power (W) | 0.093 | 0.220 | 0.262 | 0.294 | 0.333 | 0.428 | 0.276 |
| T_pipe average | -18.6 | -17.8 | -16.6 | -15.6 | -14.6 | -12.2 | -16 |
| P_stave (bar) | 2.05 | 2.05 | 2.23 | 2.41 | 2.6 | 2.6 | 2.05 |
| T from P_stave | -20.0 | -20.0 | -17.9 | -15.8 | -13.6 | -13.6 | -20.0 |
| T hybrid block | -17.3 | -7.6 | -6.2 | -5.2 | -4.1 | -2.3 | -6.1 |
| T detector block | -17.7 | -9.1 | -7.8 | -6.7 | -5.5 | -3.7 | -7.8 |
| T box | -2.3 | -2 | -1.7 | -1.6 | -1.6 | 1.9 | 2.4 |
| T nitrogen | -12.1 | -12.1 | -12.1 | -12.9 | -12.7 | 2.5 | 0.3 |
| T wings average | -13.5 | -7.5 | -6.3 | -5.4 | -4.5 | -2.1 | -5 |
| I scale factor to 0 C | 0.268 | 0.512 | 0.557 | 0.625 | 0.700 | 0.825 | 0.599 |
| P dens (W/m^2 at 0 C) | 56 | 70 | 76 | 76 | 77 | 84 | 75 |
| T det from I det | -17.9 | -9.7 | -7.4 | -6.5 | -5.7 | -2.1 input | -7.9 |

Table 2. Results from the module test.

Our experimental results are shown in Table 2 and discussed below. After the first run with LV off , the hybrid power was constant at 6.4 W. The detector bias was 450 V in all runs and the resulting leakage current and power are shown in the table. The next row shows the average of the input and output pipe temperatures. Below this we report the pressure measured in the stave and the coolant temperature derived from this pressure as described in the section on HTC measurement. The difference between “T from P_stave” and “T_pipe average” is clearly correlated with the pipe temperature relative to the nitrogen, indicating that the gas environment is influencing the temperature of the sensors, as we have seen before and by now expect. The sensors on the blocks and the wings will also be influenced by the environment in a similar way so we can not take their readings at face value. The box temperature was significantly warmer than in [2] because the freezer lid was not tightly shut and was leaking warm air onto the module box.

Runs 9b to 9e show what happened as we increased the coolant temperature as far as it would go. It was not possible to go above 2.5 bar at the collection tank, giving 2.6 bar on the stave and a coolant temperature in the module box of around –13 C. The module was clearly still far from thermal runaway and we were concerned that it might be cooled significantly by the nitrogen. Therefore we switched off the freezer and opened its lid, allowing the box and the nitrogen to warm up well above the module temperature. Run 9f shows these conditions, where we can be sure that heat is flowing from the environment to the module and not the other way.

The last three lines of the table show an analysis of the detector temperature based on the assumption that in run 9f the wing average temperature is a good measure of the detector temperature. This is a reasonable assumption because the wings are close to the environment temperature in this run. The expected ratio between leakage current at the wing average temperature and at 0 C is shown on the next line. The result of scaling the measured detector power to 0 C and normalising to the area of 0.00618 m^2 is shown on the penultimate line. We take the value of 84 W/m^2 at 0 C to be correct. The expected value after 31014 protons irradiation and one week of room temperature annealing is 98 W/m^2 at 0 C; reasonably consistent given the extra annealing that this module experienced. The last line shows the detector temperature derived from the leakage current value, assuming an energy gap of 1.2 eV.

### Conclusion on safety factor.

In Run 9f the coolant temperature was around –13 C, the hybrid power and detector bias were very close to their maximum specified values, there was a positive heat load on the detector from the environment and the detector was not in thermal runaway. The detector radiation damage was 84 W/m^2 at 0 C whereas the maximum value that we can expect in Atlas after 10 years is 185 W/m^2 at 0 C. The temperature reduction that is necessary to reduce leakage current by a factor 84/185 is 8.4 degrees. Therefore if we reduced the coolant temperature by this amount and simultaneously increased the radiation damage to

the Atlas maximum, then the detectors temperature relative to the coolant would be unchanged: the coolant would be at around –22 and the detectors at around –11 C.

This estimate does not take account of the convective heat load of up to 0.4 W which is expected on inner modules at the worst positions on the disk. According to previous measurements of thermal resistance on the inner module ( 4.5 K/W between detector and block) this would increase the detector temperature by about 2 degrees. The heat load in the test box was probably much lower than 0.4 W. On the other hand we did not reach runaway so we may have had a few extra degrees of safety there.

## References

[1] Information on C3F8 by Vic Vacek at http://st-support-cooling-electronics.web.cern.ch/st-support-cooling-electronics/CWGWeb/C3F8.htm

[2] Thermal Measurements on K5-313 at the RAL Evaporative Cooling Rig. Mauro Donega, Stephen Haywood, Rainer Wallny, Ian Wilmut.