CRITICAL ANALYSIS OF THE HEATER TESTS

AND EXTRAPOLATION TO FINAL HEATER DESIGN

# 1. Scope

The scope of this short note is to analyze the results of the test of the two heater prototypes with the aim of understanding their performances and of extrapolating the final heater design.

The detailed description and analysis of the heater test is in a separate document, here we focus just on the critical parameters allowing for extrapolating the final design.

# 2. Introductions and description of heaters

Two types of heaters have been fabricated by Thermocoax company according to the drawings:

- 302038 (small size): ZKZ Ac 11.5/50-466-50 model

- 302037 (big size): ZEZ Ac 20/50-379-50

The major parameters of these two prototypes are given in the following table:

|  |  | HEATER TYPE |  |
| --- | --- | --- | --- |
|  | UNITs | ZKZ Ac 11.5/50-466-50 | ZEZ Ac 20/50-379-50 |
| Length of heating element | mm | 4660 | 3790 |
| Length of coil | mm | 460 | 460 |
| Diameter of heating element | mm | 1.15 | 2 |
| Inner tube diameter | mm | 7 | 12 |
| Free internal diameter | mm | 4.7 | 8 |
| Average coil diameter | mm | 5.85 | 10 |
| n. of coils |  | 253 | 120 |
| Pitch of spiral | mm | 1.8 | 3.8 |
| Gap between spirals | mm | 0.66 | 1.8 |
| Nominal power (at 100V) | W | 506 | 810 |
| Contact area | cm2 | 168 | 238 |
| Specific surface heat load | W/cm2 | 3.0 | 3.4 |

# 3. Test results

## 3.1 Temperatures

Several tests have been performed on the prototypes.

The parameters, which are critical for the operation of the heaters, are:

- maximum temperature of the heating element, both during steady state running and during transient conditions

- the pressure drops across the heater: current budget is 50 mbar

Scope of the heater is to raise the vapor temperature at the exhaust to 20 C.

The max outer temperature of the heater is always only slightly above the exhaust vapor temperature so it is not an issue.

The temperature of the heating element is higher when the power on the staves is switched OFF, so only the steady state case with max power of the heater is analyzed.

The heater temperature is always referred to as the maximum (at the vapor exit).

The following table summarizes the measured temperatures during tests of the small heater:

|  |  |  |  | Steady state |  |  |  | Transient |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Max Power set [W] | Duty Cycle [%] | Average power [W] | Vapor T at the exhaust | Average T of heating element | Max pick T of heating element | DT between heating element and exhaust fluid | Max T excursion during steady state regulation | Max pick temp. (0-100 of power load) |
| 640 | 91 | 582 | 27 | 45 | 55 | 18 | +/-10 | 65 |
| 640 | 73 | 480 | 22 | 38 | 48 | 16 | +/-10 | 60 |
| 350 | 73 | 256 | 25 | 39 | 44 | 14 | +/-5 | 60 |

Chart 1 shows the temperature difference between the heating element and the fluid (exhaust vapor) as function of the power.

Chart 1 also shows the calculated temperature curve (linear) assuming the heat transfer coefficient between the fluid and heating element does not change with the power.

In reality the heat transfer coefficient changes with the flow (which is linear with the power assuming, as it is the case, always the same inlet vapor quality at the inlet of the heater). For monophase (gas) turbulent flow the non dimensional correlation governing the heat transfer is:

Nu=0.023Re 0.8

Where: Nu is the Nusselt number and Re is the Reynolds number

From this correlation the heat transfer coefficient can be expresses as function of the volumetric flow and of the diameter, thus giving the following equation:

h= f(D-1.8Q0.8)

where: h is the heat transfer coefficient and Q is the volumetric flow.

Chart 1 shows temperature change calculated according to this formula normalizing to the max power point and the agreement found with the experimental data is very good.

Increasing the power the flow increases and counterbalance, with the increase of the heat transfer coefficient, the increase of the temperature gradient heater-fluid, thus reducing the slope of the curve.

Similar measurements will be performed on the big heater.

## 3.2 Pressure drops

The pressure drops across were measured for both types of heaters.

The results are shown in chart 2.

The pressure drops are linear with the mass flow.

For both heaters the pressure drops are above the specifications. To decrease the pressure drops, in particular for the small heater, to within the specification the free internal diameter of the heater has to be increased.

The following table 3 gives the predicted free diameter required to decrease the pressure drops to 50 mbar. The extrapolation is extended to all the circuits and assumes that the 1.15 mm heating element is adopted also for the max power

| Table 3: heater design parameters |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Extrapolated heater |  |  |  |
| circuit | Power load | Nominal Mass flow (per circuit) | Max heater power with nominal flow | Heater design power (1) | Pressure drops with current design | Pressure drops | Free diameter | Tube diameter | Heating element |
|  | W | g/s | W | W | mbar | mbar | mm | mm | Thermocoax |
| SCT Barrel | 504 | 7.8 | 700 | 960 | 101 | 41 | 10 | 14/15 | ZEZ Ac 20/50-320-50 |
| SCT EC (3 sectors disk) | 346.5 | 5.3 | 475 | 650 | 430 | 37 | 8.7 | 11/12 | ZKZ Ac 11.5/50-363-50 |
| Pixel service panels | 250 | 4.5 | 404 | 560 | 328 | 28 | 8.7 | 11/12 | ZKZ Ac 11.5/50-421-50 |
| Pixel Barrel | 220 | 3.9 | 350 | 480 | 252 | 30 | 8 | 10/12 | ZKZ Ac 10/50-374-50 |
| SCT EC (2 sectors disk) | 241.5 | 3.7 | 333 | 480 | 227 | 27 | 8 | 10/12 | ZKZ Ac 10/50-374-50 |
| SCT EC (1 sectors disk) | 136.5 | 2.1 | 188 | 260 | 25 | 20 | 5 | 7/8 | ZKZ Ac 10/50-413-50 |
| Pixel Discs | 110 | 2.0 | 180 | 260 | 14 | 11 | 5 | 7/8 | ZKZ Ac 10/50-413-50 |
| SCT EC outer thermal enclosure | 525 | 8.0 | 700 | 840 | On hold waiting for final decision on the thermal enclosure design |  |  |  |  |
| SCT rear end thermal enclosure | 220 | 3.3 | 292 | 350 |  |  |  |  |  |
| SCT barrel thermal enclosure | 216 | 3.3 | 292 | 350 |  |  |  |  |  |

- Max heater power (corresponding to no power load on the structures and to 20% of mass flow increase) + design margin

In the document on the specification of the evaporative system it is stated that the heater is designed for a power corresponding to the nominal flow + 20% (anticipated increase from full to no detector load conditions). However for the calculation of the pressure drops, which are relevant only when the detector is operating at full power, we assume the nominal flow.

Basing on the extrapolation of the heater design as per table 3 and according to the interpretation of the temperature measurements it is possible to estimate the working conditions of the heater.

This estimate has been done extrapolating from the measurements according to the following calculation method:

The temperature difference between the heating element and the coolant for monophase flow (end of the heater) is given by:

T=P/(hA)

Where A is the contact area per unit of length, P the power per unit of length and h is the convective heat transfer coefficient.

Combining equation (2) with (1) and recalling that the volumetric flow is directly proportional to the power the following equation is extracted, which is used for the extrapolation:

T1/T0=(P1/P0)0.2(D1/D0)0.8A0/A1

Table 4 gives the extrapolated operation temperatures for the various types of heaters.

| Circuit | Heater type | Length of heating element | Diameter of heating element | Contact area | Maximum heater power with nominal flow | Free diameter | Specific surface heat load | Expected temperature gradient (heater surface - fluid |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | mm | mm | cm2 | W | mm | W/cm2 | C |
|  | Tested heater prototype | 4660 | 1.15 | 168 | 480 | 4.7 | 3 | 16 |
| SCT Barrel | ZEZ Ac 20/50-320-50 | 3200 | 2 | 200 | 700 | 10 | 3.5 | 27 |
| SCT EC (3 sectors disk) | ZKZ Ac 11.5/50-363-50 | 3630 | 1.15 | 131 | 475 | 8.7 | 3.6 | 34 |
| Pixel service panels | ZKZ Ac 11.5/50-421-50 | 4210 | 1.15 | 152 | 404 | 8.7 | 2.7 | 28 |
| Pixel Barrel | ZKZ Ac 10/50-374-50 | 3740 | 1 | 117 | 350 | 8 | 3 | 33 |
| SCT EC (2 sectors disk) | ZKZ Ac 10/50-374-50 | 3740 | 1 | 117 | 333 | 8 | 2.8 | 33 |
| SCT EC (1 sectors disk) | ZKZ Ac 10/50-413-50 | 4130 | 1 | 130 | 188 | 5 | 1.5 | 18 |
| Pixel Discs | ZKZ Ac 10/50-413-50 | 4130 | 1 | 130 | 180 | 5 | 1.4 | 18 |

Assuming as nominal vapor return temperature 20 C the average operating temperature of heater would then be in the worst case 54 C with an expected pick temperature of 64 C.

All these temperatures are well below the max acceptable limits of both the heater design and of the coolant.