## Sheet1
| load |  |  |  |  | HEX details | [7 empty] | HEATER | [6 empty] | from control PC
|  | pressure |  |  | mass flow | pressures |  |  |  | temperatures |  |  |  | pressures |  | temps |  |  |  |  | power | heater wire | heater ext | vapour | set point
date:time |  | back pressure | before BPR | liquid pressure |  | liquid in | liquid out | vapour in | vapout out | liquid in | liquid out | vapour in | vapout out | before heater | diff | before heater | 1 | 2 | 3 | after (14cm) |  | temp | temp | temp | temp
started heater recording data heater set to 620W
14:50 | 0% | 1.625 | 1.73 | 14 | 3.33 | 13.8 | 13.7 | 1.88 | 1.86 | 19.45 | -13.21 | -24.14 | -22.29 | 1.88 | 0.17 | -21.75 | -21.7 | -1.4 | 29.49 | 27.75 | 38.5% | 40-50 | 30 | 29 | 30
comment: | massflow => heater design power of 350W
| P=V^2R | V =
| R=19.3 | 82.1888
set heater to 350W (V=82)
15:38 | 0% | 1.62 | 1.71 | 14 | 3.39 | 13.8 | 13.6 | 1.88 | 1.86 | 19.65 | -13.17 | -24.16 | -22.34 | 1.9 | 0.19 | -21.75 | -21.86 | -2.06 | 27.94 | 27.5 | 84% | 40-50 | 30 | 29 | 30
(scan 496)
set heat load to 100% |  | P=220W, R=66.1 V= |  | 120.5902 | 3.14
15:57 | 100%
(scan600)
not stable temp of liquid from HEX getting higher
16:21 | decreased the heat load to 200W, V=115 |  |  | temps fall, wait for stability to make measurements
(scan780)? | 91% | 1.6 | 1.7 | 14 | 3.26 | 13.75 | 13.6 | 1.88 | 1.86 | 19.79 | -8.38 | -20.73 | 0.05 | 1.9 | 0.19 | 2.14 | 9.41 | 18.91 | 27.95 | 27.78 | 20% | 30-40 | 30 | 30 | 30
reached 1000 scans - stopped and restared pvss
17:16
(scan 30) | 91% | 1.6 | 1.7 | 14 | 3.33 | 13.8 | 13.6 | 1.88 | 1.86 | 19.72 | -10.01 | -20.74 | -2.25 | 1.89 | 0.19 | 0.08 | 7.33 | 18.55 | 28.07 | 27.68 | 23% | 30-40 | 30 | 30 | 30
turned power OFF 0%
17:20 | 0% | 1.65 | 1.73 | 14 | 3.26 | 13.75 | 13.6 | 1.88 | 1.86 | 19.71 | -13.16 | -24.13 | -22.3 | 1.9 | 0.19 | -21.61 | -21.64 | -1.27 | 28.25 | 27.86 | 75% | 40-50 | 30 | 30 | 30
(scan54) |  |  |  | if bar = 0.51 | 3.33
changed setpoint to 25C
17:41 | 0%
(scan190)
turned off system
do this experiment tomorrow