## Sheet1
| load |  |  |  |  | HEX details | [7 empty] | HEATER | [6 empty] | from control PC
|  | pressure |  |  | mass flow | pressures |  |  |  | temperatures |  |  |  | pressures |  | temps |  |  |  |  | power | heater wire | heater ext | vapour | set point
date:time |  | back pressure | before BPR | liquid pressure |  | liquid in | liquid out | vapour in | vapout out | liquid in | liquid out | vapour in | vapout out | before heater | diff | before heater | 1 | 2 | 3 | after (14cm) |  | temp | temp | temp | temp
now looking at system with the set-point of the heater set to 25C rather than 30C
(yesterday started with these settings) |  |  |  | heater at 620W
14:50 | 0% | 1.625 | 1.73 | 14 | 3.33 | 13.8 | 13.7 | 1.88 | 1.86 | 19.45 | -13.21 | -24.14 | -22.29 | 1.88 | 0.17 | -21.75 | -21.7 | -1.4 | 29.49 | 27.75 | 38.5% | 40-50 | 30 | 29 | 30
now re-measureing system with heater at 620W to get mass flow of this morning
started heater data capture at 10:04
10:12 | 0% | 1.64 | 1.72 | 13.6 | 3.36 | 13.5 | 13.3 | 1.88 | 1.86 | 18.55 | -13.41 | -24.07 | -22.26 | 1.89 | 0.17 | -21.78 | -21.53 | -7.02 | 23.99 | 22.48 | 47% | 35-45 | 25 | 24 | 25
(scan313)
10:22 | 0% |  | 1.72 | 13.6 |  | 13.5 | 13.3 | 1.89 | 1.87 | 18.42 | -13.46 | -24.05 | -22.31 | 1.89 | 0.18 | -21.72 | -21.63 | -13.7 | 23.33 | 22.65 | 48% | 35-45 | 25 | 24 | 25
okay mass flow about the same as yesterday (3.33) and stable conditions
turn heater to 350W, V=82
comment: | massflow => heater design power of 350W
| P=V^2R | V =
| R=19.3 | 82.1888
set heater to 350W (V=82) | [20 empty] | jump in heater output as it finds opperating point
10:24 | 0% | 1.625 | 1.71 | 13.7 | 3.3 | 13.5 | 13.25 | 1.88 | 1.87 | 18.55 | -13.42 | -24.01 | -22.34 | 1.88 | 0.17 | -21.79 | -21.69 | -6.73 | 24.5 | 22.23 | 77% | 35-45 | 25 | 24.5 | 25
(scan388)
jump the power of the load to 200W |  |  | V=115
10:40 | 91% | 1.62 | 1.7 | 13.6 | 3.26 | 13.45 | 13.3 | 1.88 | 1.86 | 18.79 | -10.46 | -20.63 | -3.05 | 1.89 | 0.18 | -1.25 | 5.16 | 14.82 | 22.81 | 22.74 | 19% | 35-25 | 25 | 24 | 25
(scan494)
stable situation, drop power to 0% | [17 empty] | varries a lot
11:03 | 0% | 1.62 | 1.73 | 13.6 | 3.28 | 13.5 | 13.25 | 1.89 | 1.86 | 18.86 | -13.4 | -24.08 | -22.25 | 1.91 | 0.17 | -21.81 | -21.79 | -14.39 | 23.27 | 22.35 | 65% | 33-43 | 25 | 24.5 | 25
(scan646) |  |  |  | bar = 0.51 | 3.35
increase power to100%, 220W V=120
11:20
(scan758)
the temperature of the inlet cooling liquid is not stable after 20 minutes.
worried that the cooling circuit might start to dry out - okay at the moment.
waiting a bit longer to see if it becomes stable
11:47 | 100% | 1.62 | 1.68 | 13.6 | 3.06 | 13.5 | 13.25 |  |  | 18.78 | 1.44 | -20.78 | 6.71 | 1.82 | 0.15 | 7.73 | 11.74 | 17.61 | 22.98 | 22.64 | 9% | 25-30 | 25 | 25 | 25
(scan761)
okay turned power off 11:49
system returns to stability
save data and turn off pvss scan 997
pvss re-started
measure system details with 0% power
12:01 | 0% | 1.61 | 1.71 | 13.6 | 3.35 | 13.5 | 13.25 | 1.89 | 1.86 | 18.82 | -13.2 | -24.11 | -22.36 | 1.9 | 0.17 | -21.79 | -21.71 | -8.09 | 23.59 | 22.41 | 71% | 35-42 | 25 | 24 | 25
(scan01)